## Modbus Table
Address Offset | Modbus Address | CoDeSys/SoMachine PLC Address |  |  |  | Vijeo HMI Address
|  | Bool | Byte | Word | Double Word | Bool | Word | Double Word
0 | 40001 | %MX0.7 - %MX0.0 | %MB0 | %MW0 | %MD0 | %MW0.X07 - %MW0.X0 | %MW0 | %MD0
1 |  | %MX1.7 - %MX1.0 | %MB1 |  |  | %MW1.X15 - %MW1.X8
2 | 40002 | %MX2.7 - %MX2.0 | %MB2 | %MW1 |  | %MW2.X07 - %MW2.X0 | %MW1
3 |  | %MX3.7 - %MX3.0 | %MB3 |  |  | %MW3.X15 - %MW3.X8
4 | 40003 | %MX4.7 - %MX4.0 | %MB4 | %MW2 | %MD1 | %MW4.X07 - %MW4.X0 | %MW2 | %MD2
5 |  | %MX5.7 - %MX5.0 | %MB5 |  |  | %MW5.X15 - %MW5.X8
6 | 40004 | %MX6.7 - %MX6.0 | %MB6 | %MW3 |  | %MW6.X07 - %MW6.X0 | %MW3
7 |  | %MX7.7 - %MX7.0 | %MB7 |  |  | %MW7.X15 - %MW7.X8
8 | 40005 | %MX8.7 - %MX8.0 | %MB8 | %MW4 | %MD2 | %MW8.X07 - %MW8.X0 | %MW4 | %MD4
9 |  | %MX9.7 - %MX9.0 | %MB9 |  |  | %MW9.X15 - %MW9.X8
10 | 40006 | %MX10.7 - %MX10.0 | %MB10 | %MW5 |  | %MW10.X07 - %MW10.X0 | %MW5
11 |  | %MX11.7 - %MX11.0 | %MB11 |  |  | %MW11.X15 - %MW11.X8
12 | 40007 | %MX12.7 - %MX12.0 | %MB12 | %MW6 | %MD3 | %MW12.X07 - %MW12.X0 | %MW6 | %MD6
13 |  | %MX13.7 - %MX13.0 | %MB13 |  |  | %MW13.X15 - %MW13.X8
14 | 40008 | %MX14.7 - %MX14.0 | %MB14 | %MW7 |  | %MW14.X07 - %MW14.X0 | %MW7
15 |  | %MX15.7 - %MX15.0 | %MB15 |  |  | %MW15.X15 - %MW15.X8
16 | 40009 | %MX16.7 - %MX16.0 | %MB16 | %MW8 | %MD4 | %MW16.X07 - %MW16.X0 | %MW8 | %MD8
17 |  | %MX17.7 - %MX17.0 | %MB17 |  |  | %MW17.X15 - %MW17.X8
18 | 40010 | %MX18.7 - %MX18.0 | %MB18 | %MW9 |  | %MW18.X07 - %MW18.X0 | %MW9
19 |  | %MX19.7 - %MX19.0 | %MB19 |  |  | %MW19.X15 - %MW19.X8
20 | 40011 | %MX20.7 - %MX20.0 | %MB20 | %MW10 | %MD5 | %MW20.X07 - %MW20.X0 | %MW10 | %MD10
21 |  | %MX21.7 - %MX21.0 | %MB21 |  |  | %MW21.X15 - %MW21.X8
22 | 40012 | %MX22.7 - %MX22.0 | %MB22 | %MW11 |  | %MW22.X07 - %MW22.X0 | %MW11
23 |  | %MX23.7 - %MX23.0 | %MB23 |  |  | %MW23.X15 - %MW23.X8
24 | 40013 | %MX24.7 - %MX24.0 | %MB24 | %MW12 | %MD6 | %MW24.X07 - %MW24.X0 | %MW12 | %MD12
25 |  | %MX25.7 - %MX25.0 | %MB25 |  |  | %MW25.X15 - %MW25.X8
26 | 40014 | %MX26.7 - %MX26.0 | %MB26 | %MW13 |  | %MW26.X07 - %MW26.X0 | %MW13
27 |  | %MX27.7 - %MX27.0 | %MB27 |  |  | %MW27.X15 - %MW27.X8
28 | 40015 | %MX28.7 - %MX28.0 | %MB28 | %MW14 | %MD7 | %MW28.X07 - %MW28.X0 | %MW14 | %MD14
29 |  | %MX29.7 - %MX29.0 | %MB29 |  |  | %MW29.X15 - %MW29.X8
30 | 40016 | %MX30.7 - %MX30.0 | %MB30 | %MW15 |  | %MW30.X07 - %MW30.X0 | %MW15
31 |  | %MX31.7 - %MX31.0 | %MB31 |  |  | %MW31.X15 - %MW31.X8
32 | 40017 | %MX32.7 - %MX32.0 | %MB32 | %MW16 | %MD8 | %MW32.X07 - %MW32.X0 | %MW16 | %MD16
33 |  | %MX33.7 - %MX33.0 | %MB33 |  |  | %MW33.X15 - %MW33.X8
34 | 40018 | %MX34.7 - %MX34.0 | %MB34 | %MW17 |  | %MW34.X07 - %MW34.X0 | %MW17
35 |  | %MX35.7 - %MX35.0 | %MB35 |  |  | %MW35.X15 - %MW35.X8
36 | 40019 | %MX36.7 - %MX36.0 | %MB36 | %MW18 | %MD9 | %MW36.X07 - %MW36.X0 | %MW18 | %MD18
37 |  | %MX37.7 - %MX37.0 | %MB37 |  |  | %MW37.X15 - %MW37.X8
38 | 40020 | %MX38.7 - %MX38.0 | %MB38 | %MW19 |  | %MW38.X07 - %MW38.X0 | %MW19
39 |  | %MX39.7 - %MX39.0 | %MB39 |  |  | %MW39.X15 - %MW39.X8
40 | 40021 | %MX40.7 - %MX40.0 | %MB40 | %MW20 | %MD10 | %MW40.X07 - %MW40.X0 | %MW20 | %MD20
41 |  | %MX41.7 - %MX41.0 | %MB41 |  |  | %MW41.X15 - %MW41.X8
42 | 40022 | %MX42.7 - %MX42.0 | %MB42 | %MW21 |  | %MW42.X07 - %MW42.X0 | %MW21
43 |  | %MX43.7 - %MX43.0 | %MB43 |  |  | %MW43.X15 - %MW43.X8
44 | 40023 | %MX44.7 - %MX44.0 | %MB44 | %MW22 | %MD11 | %MW44.X07 - %MW44.X0 | %MW22 | %MD22
45 |  | %MX45.7 - %MX45.0 | %MB45 |  |  | %MW45.X15 - %MW45.X8
46 | 40024 | %MX46.7 - %MX46.0 | %MB46 | %MW23 |  | %MW46.X07 - %MW46.X0 | %MW23
47 |  | %MX47.7 - %MX47.0 | %MB47 |  |  | %MW47.X15 - %MW47.X8
48 | 40025 | %MX48.7 - %MX48.0 | %MB48 | %MW24 | %MD12 | %MW48.X07 - %MW48.X0 | %MW24 | %MD24
49 |  | %MX49.7 - %MX49.0 | %MB49 |  |  | %MW49.X15 - %MW49.X8
50 | 40026 | %MX50.7 - %MX50.0 | %MB50 | %MW25 |  | %MW50.X07 - %MW50.X0 | %MW25
51 |  | %MX51.7 - %MX51.0 | %MB51 |  |  | %MW51.X15 - %MW51.X8
52 | 40027 | %MX52.7 - %MX52.0 | %MB52 | %MW26 | %MD13 | %MW52.X07 - %MW52.X0 | %MW26 | %MD26
53 |  | %MX53.7 - %MX53.0 | %MB53 |  |  | %MW53.X15 - %MW53.X8
54 | 40028 | %MX54.7 - %MX54.0 | %MB54 | %MW27 |  | %MW54.X07 - %MW54.X0 | %MW27
55 |  | %MX55.7 - %MX55.0 | %MB55 |  |  | %MW55.X15 - %MW55.X8
56 | 40029 | %MX56.7 - %MX56.0 | %MB56 | %MW28 | %MD14 | %MW56.X07 - %MW56.X0 | %MW28 | %MD28
57 |  | %MX57.7 - %MX57.0 | %MB57 |  |  | %MW57.X15 - %MW57.X8
58 | 40030 | %MX58.7 - %MX58.0 | %MB58 | %MW29 |  | %MW58.X07 - %MW58.X0 | %MW29
59 |  | %MX59.7 - %MX59.0 | %MB59 |  |  | %MW59.X15 - %MW59.X8
60 | 40031 | %MX60.7 - %MX60.0 | %MB60 | %MW30 | %MD15 | %MW60.X07 - %MW60.X0 | %MW30 | %MD30
61 |  | %MX61.7 - %MX61.0 | %MB61 |  |  | %MW61.X15 - %MW61.X8
62 | 40032 | %MX62.7 - %MX62.0 | %MB62 | %MW31 |  | %MW62.X07 - %MW62.X0 | %MW31
63 |  | %MX63.7 - %MX63.0 | %MB63 |  |  | %MW63.X15 - %MW63.X8
64 | 40033 | %MX64.7 - %MX64.0 | %MB64 | %MW32 | %MD16 | %MW64.X07 - %MW64.X0 | %MW32 | %MD32
65 |  | %MX65.7 - %MX65.0 | %MB65 |  |  | %MW65.X15 - %MW65.X8
66 | 40034 | %MX66.7 - %MX66.0 | %MB66 | %MW33 |  | %MW66.X07 - %MW66.X0 | %MW33
67 |  | %MX67.7 - %MX67.0 | %MB67 |  |  | %MW67.X15 - %MW67.X8
68 | 40035 | %MX68.7 - %MX68.0 | %MB68 | %MW34 | %MD17 | %MW68.X07 - %MW68.X0 | %MW34 | %MD34
69 |  | %MX69.7 - %MX69.0 | %MB69 |  |  | %MW69.X15 - %MW69.X8
70 | 40036 | %MX70.7 - %MX70.0 | %MB70 | %MW35 |  | %MW70.X07 - %MW70.X0 | %MW35
71 |  | %MX71.7 - %MX71.0 | %MB71 |  |  | %MW71.X15 - %MW71.X8
72 | 40037 | %MX72.7 - %MX72.0 | %MB72 | %MW36 | %MD18 | %MW72.X07 - %MW72.X0 | %MW36 | %MD36
73 |  | %MX73.7 - %MX73.0 | %MB73 |  |  | %MW73.X15 - %MW73.X8
74 | 40038 | %MX74.7 - %MX74.0 | %MB74 | %MW37 |  | %MW74.X07 - %MW74.X0 | %MW37
75 |  | %MX75.7 - %MX75.0 | %MB75 |  |  | %MW75.X15 - %MW75.X8
76 | 40039 | %MX76.7 - %MX76.0 | %MB76 | %MW38 | %MD19 | %MW76.X07 - %MW76.X0 | %MW38 | %MD38
77 |  | %MX77.7 - %MX77.0 | %MB77 |  |  | %MW77.X15 - %MW77.X8
78 | 40040 | %MX78.7 - %MX78.0 | %MB78 | %MW39 |  | %MW78.X07 - %MW78.X0 | %MW39
79 |  | %MX79.7 - %MX79.0 | %MB79 |  |  | %MW79.X15 - %MW79.X8
80 | 40041 | %MX80.7 - %MX80.0 | %MB80 | %MW40 | %MD20 | %MW80.X07 - %MW80.X0 | %MW40 | %MD40
81 |  | %MX81.7 - %MX81.0 | %MB81 |  |  | %MW81.X15 - %MW81.X8
82 | 40042 | %MX82.7 - %MX82.0 | %MB82 | %MW41 |  | %MW82.X07 - %MW82.X0 | %MW41
83 |  | %MX83.7 - %MX83.0 | %MB83 |  |  | %MW83.X15 - %MW83.X8
84 | 40043 | %MX84.7 - %MX84.0 | %MB84 | %MW42 | %MD21 | %MW84.X07 - %MW84.X0 | %MW42 | %MD42
85 |  | %MX85.7 - %MX85.0 | %MB85 |  |  | %MW85.X15 - %MW85.X8
86 | 40044 | %MX86.7 - %MX86.0 | %MB86 | %MW43 |  | %MW86.X07 - %MW86.X0 | %MW43
87 |  | %MX87.7 - %MX87.0 | %MB87 |  |  | %MW87.X15 - %MW87.X8
88 | 40045 | %MX88.7 - %MX88.0 | %MB88 | %MW44 | %MD22 | %MW88.X07 - %MW88.X0 | %MW44 | %MD44
89 |  | %MX89.7 - %MX89.0 | %MB89 |  |  | %MW89.X15 - %MW89.X8
90 | 40046 | %MX90.7 - %MX90.0 | %MB90 | %MW45 |  | %MW90.X07 - %MW90.X0 | %MW45
91 |  | %MX91.7 - %MX91.0 | %MB91 |  |  | %MW91.X15 - %MW91.X8
92 | 40047 | %MX92.7 - %MX92.0 | %MB92 | %MW46 | %MD23 | %MW92.X07 - %MW92.X0 | %MW46 | %MD46
93 |  | %MX93.7 - %MX93.0 | %MB93 |  |  | %MW93.X15 - %MW93.X8
94 | 40048 | %MX94.7 - %MX94.0 | %MB94 | %MW47 |  | %MW94.X07 - %MW94.X0 | %MW47
95 |  | %MX95.7 - %MX95.0 | %MB95 |  |  | %MW95.X15 - %MW95.X8
96 | 40049 | %MX96.7 - %MX96.0 | %MB96 | %MW48 | %MD24 | %MW96.X07 - %MW96.X0 | %MW48 | %MD48
97 |  | %MX97.7 - %MX97.0 | %MB97 |  |  | %MW97.X15 - %MW97.X8
98 | 40050 | %MX98.7 - %MX98.0 | %MB98 | %MW49 |  | %MW98.X07 - %MW98.X0 | %MW49
99 |  | %MX99.7 - %MX99.0 | %MB99 |  |  | %MW99.X15 - %MW99.X8
100 | 40051 | %MX100.7 - %MX100.0 | %MB100 | %MW50 | %MD25 | %MW100.X07 - %MW100.X0 | %MW50 | %MD50
101 |  | %MX101.7 - %MX101.0 | %MB101 |  |  | %MW101.X15 - %MW101.X8
102 | 40052 | %MX102.7 - %MX102.0 | %MB102 | %MW51 |  | %MW102.X07 - %MW102.X0 | %MW51
103 |  | %MX103.7 - %MX103.0 | %MB103 |  |  | %MW103.X15 - %MW103.X8
104 | 40053 | %MX104.7 - %MX104.0 | %MB104 | %MW52 | %MD26 | %MW104.X07 - %MW104.X0 | %MW52 | %MD52
105 |  | %MX105.7 - %MX105.0 | %MB105 |  |  | %MW105.X15 - %MW105.X8
106 | 40054 | %MX106.7 - %MX106.0 | %MB106 | %MW53 |  | %MW106.X07 - %MW106.X0 | %MW53
107 |  | %MX107.7 - %MX107.0 | %MB107 |  |  | %MW107.X15 - %MW107.X8
108 | 40055 | %MX108.7 - %MX108.0 | %MB108 | %MW54 | %MD27 | %MW108.X07 - %MW108.X0 | %MW54 | %MD54
109 |  | %MX109.7 - %MX109.0 | %MB109 |  |  | %MW109.X15 - %MW109.X8
110 | 40056 | %MX110.7 - %MX110.0 | %MB110 | %MW55 |  | %MW110.X07 - %MW110.X0 | %MW55
111 |  | %MX111.7 - %MX111.0 | %MB111 |  |  | %MW111.X15 - %MW111.X8
112 | 40057 | %MX112.7 - %MX112.0 | %MB112 | %MW56 | %MD28 | %MW112.X07 - %MW112.X0 | %MW56 | %MD56
113 |  | %MX113.7 - %MX113.0 | %MB113 |  |  | %MW113.X15 - %MW113.X8
114 | 40058 | %MX114.7 - %MX114.0 | %MB114 | %MW57 |  | %MW114.X07 - %MW114.X0 | %MW57
115 |  | %MX115.7 - %MX115.0 | %MB115 |  |  | %MW115.X15 - %MW115.X8
116 | 40059 | %MX116.7 - %MX116.0 | %MB116 | %MW58 | %MD29 | %MW116.X07 - %MW116.X0 | %MW58 | %MD58
117 |  | %MX117.7 - %MX117.0 | %MB117 |  |  | %MW117.X15 - %MW117.X8
118 | 40060 | %MX118.7 - %MX118.0 | %MB118 | %MW59 |  | %MW118.X07 - %MW118.X0 | %MW59
119 |  | %MX119.7 - %MX119.0 | %MB119 |  |  | %MW119.X15 - %MW119.X8
120 | 40061 | %MX120.7 - %MX120.0 | %MB120 | %MW60 | %MD30 | %MW120.X07 - %MW120.X0 | %MW60 | %MD60
121 |  | %MX121.7 - %MX121.0 | %MB121 |  |  | %MW121.X15 - %MW121.X8
122 | 40062 | %MX122.7 - %MX122.0 | %MB122 | %MW61 |  | %MW122.X07 - %MW122.X0 | %MW61
123 |  | %MX123.7 - %MX123.0 | %MB123 |  |  | %MW123.X15 - %MW123.X8
124 | 40063 | %MX124.7 - %MX124.0 | %MB124 | %MW62 | %MD31 | %MW124.X07 - %MW124.X0 | %MW62 | %MD62
125 |  | %MX125.7 - %MX125.0 | %MB125 |  |  | %MW125.X15 - %MW125.X8
126 | 40064 | %MX126.7 - %MX126.0 | %MB126 | %MW63 |  | %MW126.X07 - %MW126.X0 | %MW63
127 |  | %MX127.7 - %MX127.0 | %MB127 |  |  | %MW127.X15 - %MW127.X8
128 | 40065 | %MX128.7 - %MX128.0 | %MB128 | %MW64 | %MD32 | %MW128.X07 - %MW128.X0 | %MW64 | %MD64
129 |  | %MX129.7 - %MX129.0 | %MB129 |  |  | %MW129.X15 - %MW129.X8
130 | 40066 | %MX130.7 - %MX130.0 | %MB130 | %MW65 |  | %MW130.X07 - %MW130.X0 | %MW65
131 |  | %MX131.7 - %MX131.0 | %MB131 |  |  | %MW131.X15 - %MW131.X8
132 | 40067 | %MX132.7 - %MX132.0 | %MB132 | %MW66 | %MD33 | %MW132.X07 - %MW132.X0 | %MW66 | %MD66
133 |  | %MX133.7 - %MX133.0 | %MB133 |  |  | %MW133.X15 - %MW133.X8
134 | 40068 | %MX134.7 - %MX134.0 | %MB134 | %MW67 |  | %MW134.X07 - %MW134.X0 | %MW67
135 |  | %MX135.7 - %MX135.0 | %MB135 |  |  | %MW135.X15 - %MW135.X8
136 | 40069 | %MX136.7 - %MX136.0 | %MB136 | %MW68 | %MD34 | %MW136.X07 - %MW136.X0 | %MW68 | %MD68
137 |  | %MX137.7 - %MX137.0 | %MB137 |  |  | %MW137.X15 - %MW137.X8
138 | 40070 | %MX138.7 - %MX138.0 | %MB138 | %MW69 |  | %MW138.X07 - %MW138.X0 | %MW69
139 |  | %MX139.7 - %MX139.0 | %MB139 |  |  | %MW139.X15 - %MW139.X8
140 | 40071 | %MX140.7 - %MX140.0 | %MB140 | %MW70 | %MD35 | %MW140.X07 - %MW140.X0 | %MW70 | %MD70
141 |  | %MX141.7 - %MX141.0 | %MB141 |  |  | %MW141.X15 - %MW141.X8
142 | 40072 | %MX142.7 - %MX142.0 | %MB142 | %MW71 |  | %MW142.X07 - %MW142.X0 | %MW71
143 |  | %MX143.7 - %MX143.0 | %MB143 |  |  | %MW143.X15 - %MW143.X8
144 | 40073 | %MX144.7 - %MX144.0 | %MB144 | %MW72 | %MD36 | %MW144.X07 - %MW144.X0 | %MW72 | %MD72
145 |  | %MX145.7 - %MX145.0 | %MB145 |  |  | %MW145.X15 - %MW145.X8
146 | 40074 | %MX146.7 - %MX146.0 | %MB146 | %MW73 |  | %MW146.X07 - %MW146.X0 | %MW73
147 |  | %MX147.7 - %MX147.0 | %MB147 |  |  | %MW147.X15 - %MW147.X8
148 | 40075 | %MX148.7 - %MX148.0 | %MB148 | %MW74 | %MD37 | %MW148.X07 - %MW148.X0 | %MW74 | %MD74
149 |  | %MX149.7 - %MX149.0 | %MB149 |  |  | %MW149.X15 - %MW149.X8
150 | 40076 | %MX150.7 - %MX150.0 | %MB150 | %MW75 |  | %MW150.X07 - %MW150.X0 | %MW75
151 |  | %MX151.7 - %MX151.0 | %MB151 |  |  | %MW151.X15 - %MW151.X8
152 | 40077 | %MX152.7 - %MX152.0 | %MB152 | %MW76 | %MD38 | %MW152.X07 - %MW152.X0 | %MW76 | %MD76
153 |  | %MX153.7 - %MX153.0 | %MB153 |  |  | %MW153.X15 - %MW153.X8
154 | 40078 | %MX154.7 - %MX154.0 | %MB154 | %MW77 |  | %MW154.X07 - %MW154.X0 | %MW77
155 |  | %MX155.7 - %MX155.0 | %MB155 |  |  | %MW155.X15 - %MW155.X8
156 | 40079 | %MX156.7 - %MX156.0 | %MB156 | %MW78 | %MD39 | %MW156.X07 - %MW156.X0 | %MW78 | %MD78
157 |  | %MX157.7 - %MX157.0 | %MB157 |  |  | %MW157.X15 - %MW157.X8
158 | 40080 | %MX158.7 - %MX158.0 | %MB158 | %MW79 |  | %MW158.X07 - %MW158.X0 | %MW79
159 |  | %MX159.7 - %MX159.0 | %MB159 |  |  | %MW159.X15 - %MW159.X8
160 | 40081 | %MX160.7 - %MX160.0 | %MB160 | %MW80 | %MD40 | %MW160.X07 - %MW160.X0 | %MW80 | %MD80
161 |  | %MX161.7 - %MX161.0 | %MB161 |  |  | %MW161.X15 - %MW161.X8
162 | 40082 | %MX162.7 - %MX162.0 | %MB162 | %MW81 |  | %MW162.X07 - %MW162.X0 | %MW81
163 |  | %MX163.7 - %MX163.0 | %MB163 |  |  | %MW163.X15 - %MW163.X8
164 | 40083 | %MX164.7 - %MX164.0 | %MB164 | %MW82 | %MD41 | %MW164.X07 - %MW164.X0 | %MW82 | %MD82
165 |  | %MX165.7 - %MX165.0 | %MB165 |  |  | %MW165.X15 - %MW165.X8
166 | 40084 | %MX166.7 - %MX166.0 | %MB166 | %MW83 |  | %MW166.X07 - %MW166.X0 | %MW83
167 |  | %MX167.7 - %MX167.0 | %MB167 |  |  | %MW167.X15 - %MW167.X8
168 | 40085 | %MX168.7 - %MX168.0 | %MB168 | %MW84 | %MD42 | %MW168.X07 - %MW168.X0 | %MW84 | %MD84
169 |  | %MX169.7 - %MX169.0 | %MB169 |  |  | %MW169.X15 - %MW169.X8
170 | 40086 | %MX170.7 - %MX170.0 | %MB170 | %MW85 |  | %MW170.X07 - %MW170.X0 | %MW85
171 |  | %MX171.7 - %MX171.0 | %MB171 |  |  | %MW171.X15 - %MW171.X8
172 | 40087 | %MX172.7 - %MX172.0 | %MB172 | %MW86 | %MD43 | %MW172.X07 - %MW172.X0 | %MW86 | %MD86
173 |  | %MX173.7 - %MX173.0 | %MB173 |  |  | %MW173.X15 - %MW173.X8
174 | 40088 | %MX174.7 - %MX174.0 | %MB174 | %MW87 |  | %MW174.X07 - %MW174.X0 | %MW87
175 |  | %MX175.7 - %MX175.0 | %MB175 |  |  | %MW175.X15 - %MW175.X8
176 | 40089 | %MX176.7 - %MX176.0 | %MB176 | %MW88 | %MD44 | %MW176.X07 - %MW176.X0 | %MW88 | %MD88
177 |  | %MX177.7 - %MX177.0 | %MB177 |  |  | %MW177.X15 - %MW177.X8
178 | 40090 | %MX178.7 - %MX178.0 | %MB178 | %MW89 |  | %MW178.X07 - %MW178.X0 | %MW89
179 |  | %MX179.7 - %MX179.0 | %MB179 |  |  | %MW179.X15 - %MW179.X8
180 | 40091 | %MX180.7 - %MX180.0 | %MB180 | %MW90 | %MD45 | %MW180.X07 - %MW180.X0 | %MW90 | %MD90
181 |  | %MX181.7 - %MX181.0 | %MB181 |  |  | %MW181.X15 - %MW181.X8
182 | 40092 | %MX182.7 - %MX182.0 | %MB182 | %MW91 |  | %MW182.X07 - %MW182.X0 | %MW91
183 |  | %MX183.7 - %MX183.0 | %MB183 |  |  | %MW183.X15 - %MW183.X8
184 | 40093 | %MX184.7 - %MX184.0 | %MB184 | %MW92 | %MD46 | %MW184.X07 - %MW184.X0 | %MW92 | %MD92
185 |  | %MX185.7 - %MX185.0 | %MB185 |  |  | %MW185.X15 - %MW185.X8
186 | 40094 | %MX186.7 - %MX186.0 | %MB186 | %MW93 |  | %MW186.X07 - %MW186.X0 | %MW93
187 |  | %MX187.7 - %MX187.0 | %MB187 |  |  | %MW187.X15 - %MW187.X8
188 | 40095 | %MX188.7 - %MX188.0 | %MB188 | %MW94 | %MD47 | %MW188.X07 - %MW188.X0 | %MW94 | %MD94
189 |  | %MX189.7 - %MX189.0 | %MB189 |  |  | %MW189.X15 - %MW189.X8
190 | 40096 | %MX190.7 - %MX190.0 | %MB190 | %MW95 |  | %MW190.X07 - %MW190.X0 | %MW95
191 |  | %MX191.7 - %MX191.0 | %MB191 |  |  | %MW191.X15 - %MW191.X8
192 | 40097 | %MX192.7 - %MX192.0 | %MB192 | %MW96 | %MD48 | %MW192.X07 - %MW192.X0 | %MW96 | %MD96
193 |  | %MX193.7 - %MX193.0 | %MB193 |  |  | %MW193.X15 - %MW193.X8
194 | 40098 | %MX194.7 - %MX194.0 | %MB194 | %MW97 |  | %MW194.X07 - %MW194.X0 | %MW97
195 |  | %MX195.7 - %MX195.0 | %MB195 |  |  | %MW195.X15 - %MW195.X8
196 | 40099 | %MX196.7 - %MX196.0 | %MB196 | %MW98 | %MD49 | %MW196.X07 - %MW196.X0 | %MW98 | %MD98
197 |  | %MX197.7 - %MX197.0 | %MB197 |  |  | %MW197.X15 - %MW197.X8
198 | 40100 | %MX198.7 - %MX198.0 | %MB198 | %MW99 |  | %MW198.X07 - %MW198.X0 | %MW99
199 |  | %MX199.7 - %MX199.0 | %MB199 |  |  | %MW199.X15 - %MW199.X8
200 | 40101 | %MX200.7 - %MX200.0 | %MB200 | %MW100 | %MD50 | %MW200.X07 - %MW200.X0 | %MW100 | %MD100
201 |  | %MX201.7 - %MX201.0 | %MB201 |  |  | %MW201.X15 - %MW201.X8
202 | 40102 | %MX202.7 - %MX202.0 | %MB202 | %MW101 |  | %MW202.X07 - %MW202.X0 | %MW101
203 |  | %MX203.7 - %MX203.0 | %MB203 |  |  | %MW203.X15 - %MW203.X8
204 | 40103 | %MX204.7 - %MX204.0 | %MB204 | %MW102 | %MD51 | %MW204.X07 - %MW204.X0 | %MW102 | %MD102
205 |  | %MX205.7 - %MX205.0 | %MB205 |  |  | %MW205.X15 - %MW205.X8
206 | 40104 | %MX206.7 - %MX206.0 | %MB206 | %MW103 |  | %MW206.X07 - %MW206.X0 | %MW103
207 |  | %MX207.7 - %MX207.0 | %MB207 |  |  | %MW207.X15 - %MW207.X8
208 | 40105 | %MX208.7 - %MX208.0 | %MB208 | %MW104 | %MD52 | %MW208.X07 - %MW208.X0 | %MW104 | %MD104
209 |  | %MX209.7 - %MX209.0 | %MB209 |  |  | %MW209.X15 - %MW209.X8
210 | 40106 | %MX210.7 - %MX210.0 | %MB210 | %MW105 |  | %MW210.X07 - %MW210.X0 | %MW105
211 |  | %MX211.7 - %MX211.0 | %MB211 |  |  | %MW211.X15 - %MW211.X8
212 | 40107 | %MX212.7 - %MX212.0 | %MB212 | %MW106 | %MD53 | %MW212.X07 - %MW212.X0 | %MW106 | %MD106
213 |  | %MX213.7 - %MX213.0 | %MB213 |  |  | %MW213.X15 - %MW213.X8
214 | 40108 | %MX214.7 - %MX214.0 | %MB214 | %MW107 |  | %MW214.X07 - %MW214.X0 | %MW107
215 |  | %MX215.7 - %MX215.0 | %MB215 |  |  | %MW215.X15 - %MW215.X8
216 | 40109 | %MX216.7 - %MX216.0 | %MB216 | %MW108 | %MD54 | %MW216.X07 - %MW216.X0 | %MW108 | %MD108
217 |  | %MX217.7 - %MX217.0 | %MB217 |  |  | %MW217.X15 - %MW217.X8
218 | 40110 | %MX218.7 - %MX218.0 | %MB218 | %MW109 |  | %MW218.X07 - %MW218.X0 | %MW109
219 |  | %MX219.7 - %MX219.0 | %MB219 |  |  | %MW219.X15 - %MW219.X8
220 | 40111 | %MX220.7 - %MX220.0 | %MB220 | %MW110 | %MD55 | %MW220.X07 - %MW220.X0 | %MW110 | %MD110
221 |  | %MX221.7 - %MX221.0 | %MB221 |  |  | %MW221.X15 - %MW221.X8
222 | 40112 | %MX222.7 - %MX222.0 | %MB222 | %MW111 |  | %MW222.X07 - %MW222.X0 | %MW111
223 |  | %MX223.7 - %MX223.0 | %MB223 |  |  | %MW223.X15 - %MW223.X8
224 | 40113 | %MX224.7 - %MX224.0 | %MB224 | %MW112 | %MD56 | %MW224.X07 - %MW224.X0 | %MW112 | %MD112
225 |  | %MX225.7 - %MX225.0 | %MB225 |  |  | %MW225.X15 - %MW225.X8
226 | 40114 | %MX226.7 - %MX226.0 | %MB226 | %MW113 |  | %MW226.X07 - %MW226.X0 | %MW113
227 |  | %MX227.7 - %MX227.0 | %MB227 |  |  | %MW227.X15 - %MW227.X8
228 | 40115 | %MX228.7 - %MX228.0 | %MB228 | %MW114 | %MD57 | %MW228.X07 - %MW228.X0 | %MW114 | %MD114
229 |  | %MX229.7 - %MX229.0 | %MB229 |  |  | %MW229.X15 - %MW229.X8
230 | 40116 | %MX230.7 - %MX230.0 | %MB230 | %MW115 |  | %MW230.X07 - %MW230.X0 | %MW115
231 |  | %MX231.7 - %MX231.0 | %MB231 |  |  | %MW231.X15 - %MW231.X8
232 | 40117 | %MX232.7 - %MX232.0 | %MB232 | %MW116 | %MD58 | %MW232.X07 - %MW232.X0 | %MW116 | %MD116
233 |  | %MX233.7 - %MX233.0 | %MB233 |  |  | %MW233.X15 - %MW233.X8
234 | 40118 | %MX234.7 - %MX234.0 | %MB234 | %MW117 |  | %MW234.X07 - %MW234.X0 | %MW117
235 |  | %MX235.7 - %MX235.0 | %MB235 |  |  | %MW235.X15 - %MW235.X8
236 | 40119 | %MX236.7 - %MX236.0 | %MB236 | %MW118 | %MD59 | %MW236.X07 - %MW236.X0 | %MW118 | %MD118
237 |  | %MX237.7 - %MX237.0 | %MB237 |  |  | %MW237.X15 - %MW237.X8
238 | 40120 | %MX238.7 - %MX238.0 | %MB238 | %MW119 |  | %MW238.X07 - %MW238.X0 | %MW119
239 |  | %MX239.7 - %MX239.0 | %MB239 |  |  | %MW239.X15 - %MW239.X8
240 | 40121 | %MX240.7 - %MX240.0 | %MB240 | %MW120 | %MD60 | %MW240.X07 - %MW240.X0 | %MW120 | %MD120
241 |  | %MX241.7 - %MX241.0 | %MB241 |  |  | %MW241.X15 - %MW241.X8
242 | 40122 | %MX242.7 - %MX242.0 | %MB242 | %MW121 |  | %MW242.X07 - %MW242.X0 | %MW121
243 |  | %MX243.7 - %MX243.0 | %MB243 |  |  | %MW243.X15 - %MW243.X8
244 | 40123 | %MX244.7 - %MX244.0 | %MB244 | %MW122 | %MD61 | %MW244.X07 - %MW244.X0 | %MW122 | %MD122
245 |  | %MX245.7 - %MX245.0 | %MB245 |  |  | %MW245.X15 - %MW245.X8
246 | 40124 | %MX246.7 - %MX246.0 | %MB246 | %MW123 |  | %MW246.X07 - %MW246.X0 | %MW123
247 |  | %MX247.7 - %MX247.0 | %MB247 |  |  | %MW247.X15 - %MW247.X8
248 | 40125 | %MX248.7 - %MX248.0 | %MB248 | %MW124 | %MD62 | %MW248.X07 - %MW248.X0 | %MW124 | %MD124
249 |  | %MX249.7 - %MX249.0 | %MB249 |  |  | %MW249.X15 - %MW249.X8
250 | 40126 | %MX250.7 - %MX250.0 | %MB250 | %MW125 |  | %MW250.X07 - %MW250.X0 | %MW125
251 |  | %MX251.7 - %MX251.0 | %MB251 |  |  | %MW251.X15 - %MW251.X8
252 | 40127 | %MX252.7 - %MX252.0 | %MB252 | %MW126 | %MD63 | %MW252.X07 - %MW252.X0 | %MW126 | %MD126
253 |  | %MX253.7 - %MX253.0 | %MB253 |  |  | %MW253.X15 - %MW253.X8
254 | 40128 | %MX254.7 - %MX254.0 | %MB254 | %MW127 |  | %MW254.X07 - %MW254.X0 | %MW127
255 |  | %MX255.7 - %MX255.0 | %MB255 |  |  | %MW255.X15 - %MW255.X8
256 | 40129 | %MX256.7 - %MX256.0 | %MB256 | %MW128 | %MD64 | %MW256.X07 - %MW256.X0 | %MW128 | %MD128
257 |  | %MX257.7 - %MX257.0 | %MB257 |  |  | %MW257.X15 - %MW257.X8
258 | 40130 | %MX258.7 - %MX258.0 | %MB258 | %MW129 |  | %MW258.X07 - %MW258.X0 | %MW129
259 |  | %MX259.7 - %MX259.0 | %MB259 |  |  | %MW259.X15 - %MW259.X8
260 | 40131 | %MX260.7 - %MX260.0 | %MB260 | %MW130 | %MD65 | %MW260.X07 - %MW260.X0 | %MW130 | %MD130
261 |  | %MX261.7 - %MX261.0 | %MB261 |  |  | %MW261.X15 - %MW261.X8
262 | 40132 | %MX262.7 - %MX262.0 | %MB262 | %MW131 |  | %MW262.X07 - %MW262.X0 | %MW131
263 |  | %MX263.7 - %MX263.0 | %MB263 |  |  | %MW263.X15 - %MW263.X8
264 | 40133 | %MX264.7 - %MX264.0 | %MB264 | %MW132 | %MD66 | %MW264.X07 - %MW264.X0 | %MW132 | %MD132
265 |  | %MX265.7 - %MX265.0 | %MB265 |  |  | %MW265.X15 - %MW265.X8
266 | 40134 | %MX266.7 - %MX266.0 | %MB266 | %MW133 |  | %MW266.X07 - %MW266.X0 | %MW133
267 |  | %MX267.7 - %MX267.0 | %MB267 |  |  | %MW267.X15 - %MW267.X8
268 | 40135 | %MX268.7 - %MX268.0 | %MB268 | %MW134 | %MD67 | %MW268.X07 - %MW268.X0 | %MW134 | %MD134
269 |  | %MX269.7 - %MX269.0 | %MB269 |  |  | %MW269.X15 - %MW269.X8
270 | 40136 | %MX270.7 - %MX270.0 | %MB270 | %MW135 |  | %MW270.X07 - %MW270.X0 | %MW135
271 |  | %MX271.7 - %MX271.0 | %MB271 |  |  | %MW271.X15 - %MW271.X8
272 | 40137 | %MX272.7 - %MX272.0 | %MB272 | %MW136 | %MD68 | %MW272.X07 - %MW272.X0 | %MW136 | %MD136
273 |  | %MX273.7 - %MX273.0 | %MB273 |  |  | %MW273.X15 - %MW273.X8
274 | 40138 | %MX274.7 - %MX274.0 | %MB274 | %MW137 |  | %MW274.X07 - %MW274.X0 | %MW137
275 |  | %MX275.7 - %MX275.0 | %MB275 |  |  | %MW275.X15 - %MW275.X8
276 | 40139 | %MX276.7 - %MX276.0 | %MB276 | %MW138 | %MD69 | %MW276.X07 - %MW276.X0 | %MW138 | %MD138
277 |  | %MX277.7 - %MX277.0 | %MB277 |  |  | %MW277.X15 - %MW277.X8
278 | 40140 | %MX278.7 - %MX278.0 | %MB278 | %MW139 |  | %MW278.X07 - %MW278.X0 | %MW139
279 |  | %MX279.7 - %MX279.0 | %MB279 |  |  | %MW279.X15 - %MW279.X8
280 | 40141 | %MX280.7 - %MX280.0 | %MB280 | %MW140 | %MD70 | %MW280.X07 - %MW280.X0 | %MW140 | %MD140
281 |  | %MX281.7 - %MX281.0 | %MB281 |  |  | %MW281.X15 - %MW281.X8
282 | 40142 | %MX282.7 - %MX282.0 | %MB282 | %MW141 |  | %MW282.X07 - %MW282.X0 | %MW141
283 |  | %MX283.7 - %MX283.0 | %MB283 |  |  | %MW283.X15 - %MW283.X8
284 | 40143 | %MX284.7 - %MX284.0 | %MB284 | %MW142 | %MD71 | %MW284.X07 - %MW284.X0 | %MW142 | %MD142
285 |  | %MX285.7 - %MX285.0 | %MB285 |  |  | %MW285.X15 - %MW285.X8
286 | 40144 | %MX286.7 - %MX286.0 | %MB286 | %MW143 |  | %MW286.X07 - %MW286.X0 | %MW143
287 |  | %MX287.7 - %MX287.0 | %MB287 |  |  | %MW287.X15 - %MW287.X8
288 | 40145 | %MX288.7 - %MX288.0 | %MB288 | %MW144 | %MD72 | %MW288.X07 - %MW288.X0 | %MW144 | %MD144
289 |  | %MX289.7 - %MX289.0 | %MB289 |  |  | %MW289.X15 - %MW289.X8
290 | 40146 | %MX290.7 - %MX290.0 | %MB290 | %MW145 |  | %MW290.X07 - %MW290.X0 | %MW145
291 |  | %MX291.7 - %MX291.0 | %MB291 |  |  | %MW291.X15 - %MW291.X8
292 | 40147 | %MX292.7 - %MX292.0 | %MB292 | %MW146 | %MD73 | %MW292.X07 - %MW292.X0 | %MW146 | %MD146
293 |  | %MX293.7 - %MX293.0 | %MB293 |  |  | %MW293.X15 - %MW293.X8
294 | 40148 | %MX294.7 - %MX294.0 | %MB294 | %MW147 |  | %MW294.X07 - %MW294.X0 | %MW147
295 |  | %MX295.7 - %MX295.0 | %MB295 |  |  | %MW295.X15 - %MW295.X8
296 | 40149 | %MX296.7 - %MX296.0 | %MB296 | %MW148 | %MD74 | %MW296.X07 - %MW296.X0 | %MW148 | %MD148
297 |  | %MX297.7 - %MX297.0 | %MB297 |  |  | %MW297.X15 - %MW297.X8
298 | 40150 | %MX298.7 - %MX298.0 | %MB298 | %MW149 |  | %MW298.X07 - %MW298.X0 | %MW149
299 |  | %MX299.7 - %MX299.0 | %MB299 |  |  | %MW299.X15 - %MW299.X8
300 | 40151 | %MX300.7 - %MX300.0 | %MB300 | %MW150 | %MD75 | %MW300.X07 - %MW300.X0 | %MW150 | %MD150
301 |  | %MX301.7 - %MX301.0 | %MB301 |  |  | %MW301.X15 - %MW301.X8
302 | 40152 | %MX302.7 - %MX302.0 | %MB302 | %MW151 |  | %MW302.X07 - %MW302.X0 | %MW151
303 |  | %MX303.7 - %MX303.0 | %MB303 |  |  | %MW303.X15 - %MW303.X8
304 | 40153 | %MX304.7 - %MX304.0 | %MB304 | %MW152 | %MD76 | %MW304.X07 - %MW304.X0 | %MW152 | %MD152
305 |  | %MX305.7 - %MX305.0 | %MB305 |  |  | %MW305.X15 - %MW305.X8
306 | 40154 | %MX306.7 - %MX306.0 | %MB306 | %MW153 |  | %MW306.X07 - %MW306.X0 | %MW153
307 |  | %MX307.7 - %MX307.0 | %MB307 |  |  | %MW307.X15 - %MW307.X8
308 | 40155 | %MX308.7 - %MX308.0 | %MB308 | %MW154 | %MD77 | %MW308.X07 - %MW308.X0 | %MW154 | %MD154
309 |  | %MX309.7 - %MX309.0 | %MB309 |  |  | %MW309.X15 - %MW309.X8
310 | 40156 | %MX310.7 - %MX310.0 | %MB310 | %MW155 |  | %MW310.X07 - %MW310.X0 | %MW155
311 |  | %MX311.7 - %MX311.0 | %MB311 |  |  | %MW311.X15 - %MW311.X8
312 | 40157 | %MX312.7 - %MX312.0 | %MB312 | %MW156 | %MD78 | %MW312.X07 - %MW312.X0 | %MW156 | %MD156
313 |  | %MX313.7 - %MX313.0 | %MB313 |  |  | %MW313.X15 - %MW313.X8
314 | 40158 | %MX314.7 - %MX314.0 | %MB314 | %MW157 |  | %MW314.X07 - %MW314.X0 | %MW157
315 |  | %MX315.7 - %MX315.0 | %MB315 |  |  | %MW315.X15 - %MW315.X8
316 | 40159 | %MX316.7 - %MX316.0 | %MB316 | %MW158 | %MD79 | %MW316.X07 - %MW316.X0 | %MW158 | %MD158
317 |  | %MX317.7 - %MX317.0 | %MB317 |  |  | %MW317.X15 - %MW317.X8
318 | 40160 | %MX318.7 - %MX318.0 | %MB318 | %MW159 |  | %MW318.X07 - %MW318.X0 | %MW159
319 |  | %MX319.7 - %MX319.0 | %MB319 |  |  | %MW319.X15 - %MW319.X8
320 | 40161 | %MX320.7 - %MX320.0 | %MB320 | %MW160 | %MD80 | %MW320.X07 - %MW320.X0 | %MW160 | %MD160
321 |  | %MX321.7 - %MX321.0 | %MB321 |  |  | %MW321.X15 - %MW321.X8
322 | 40162 | %MX322.7 - %MX322.0 | %MB322 | %MW161 |  | %MW322.X07 - %MW322.X0 | %MW161
323 |  | %MX323.7 - %MX323.0 | %MB323 |  |  | %MW323.X15 - %MW323.X8
324 | 40163 | %MX324.7 - %MX324.0 | %MB324 | %MW162 | %MD81 | %MW324.X07 - %MW324.X0 | %MW162 | %MD162
325 |  | %MX325.7 - %MX325.0 | %MB325 |  |  | %MW325.X15 - %MW325.X8
326 | 40164 | %MX326.7 - %MX326.0 | %MB326 | %MW163 |  | %MW326.X07 - %MW326.X0 | %MW163
327 |  | %MX327.7 - %MX327.0 | %MB327 |  |  | %MW327.X15 - %MW327.X8
328 | 40165 | %MX328.7 - %MX328.0 | %MB328 | %MW164 | %MD82 | %MW328.X07 - %MW328.X0 | %MW164 | %MD164
329 |  | %MX329.7 - %MX329.0 | %MB329 |  |  | %MW329.X15 - %MW329.X8
330 | 40166 | %MX330.7 - %MX330.0 | %MB330 | %MW165 |  | %MW330.X07 - %MW330.X0 | %MW165
331 |  | %MX331.7 - %MX331.0 | %MB331 |  |  | %MW331.X15 - %MW331.X8
332 | 40167 | %MX332.7 - %MX332.0 | %MB332 | %MW166 | %MD83 | %MW332.X07 - %MW332.X0 | %MW166 | %MD166
333 |  | %MX333.7 - %MX333.0 | %MB333 |  |  | %MW333.X15 - %MW333.X8
334 | 40168 | %MX334.7 - %MX334.0 | %MB334 | %MW167 |  | %MW334.X07 - %MW334.X0 | %MW167
335 |  | %MX335.7 - %MX335.0 | %MB335 |  |  | %MW335.X15 - %MW335.X8
336 | 40169 | %MX336.7 - %MX336.0 | %MB336 | %MW168 | %MD84 | %MW336.X07 - %MW336.X0 | %MW168 | %MD168
337 |  | %MX337.7 - %MX337.0 | %MB337 |  |  | %MW337.X15 - %MW337.X8
338 | 40170 | %MX338.7 - %MX338.0 | %MB338 | %MW169 |  | %MW338.X07 - %MW338.X0 | %MW169
339 |  | %MX339.7 - %MX339.0 | %MB339 |  |  | %MW339.X15 - %MW339.X8
340 | 40171 | %MX340.7 - %MX340.0 | %MB340 | %MW170 | %MD85 | %MW340.X07 - %MW340.X0 | %MW170 | %MD170
341 |  | %MX341.7 - %MX341.0 | %MB341 |  |  | %MW341.X15 - %MW341.X8
342 | 40172 | %MX342.7 - %MX342.0 | %MB342 | %MW171 |  | %MW342.X07 - %MW342.X0 | %MW171
343 |  | %MX343.7 - %MX343.0 | %MB343 |  |  | %MW343.X15 - %MW343.X8
344 | 40173 | %MX344.7 - %MX344.0 | %MB344 | %MW172 | %MD86 | %MW344.X07 - %MW344.X0 | %MW172 | %MD172
345 |  | %MX345.7 - %MX345.0 | %MB345 |  |  | %MW345.X15 - %MW345.X8
346 | 40174 | %MX346.7 - %MX346.0 | %MB346 | %MW173 |  | %MW346.X07 - %MW346.X0 | %MW173
347 |  | %MX347.7 - %MX347.0 | %MB347 |  |  | %MW347.X15 - %MW347.X8
348 | 40175 | %MX348.7 - %MX348.0 | %MB348 | %MW174 | %MD87 | %MW348.X07 - %MW348.X0 | %MW174 | %MD174
349 |  | %MX349.7 - %MX349.0 | %MB349 |  |  | %MW349.X15 - %MW349.X8
350 | 40176 | %MX350.7 - %MX350.0 | %MB350 | %MW175 |  | %MW350.X07 - %MW350.X0 | %MW175
351 |  | %MX351.7 - %MX351.0 | %MB351 |  |  | %MW351.X15 - %MW351.X8
352 | 40177 | %MX352.7 - %MX352.0 | %MB352 | %MW176 | %MD88 | %MW352.X07 - %MW352.X0 | %MW176 | %MD176
353 |  | %MX353.7 - %MX353.0 | %MB353 |  |  | %MW353.X15 - %MW353.X8
354 | 40178 | %MX354.7 - %MX354.0 | %MB354 | %MW177 |  | %MW354.X07 - %MW354.X0 | %MW177
355 |  | %MX355.7 - %MX355.0 | %MB355 |  |  | %MW355.X15 - %MW355.X8
356 | 40179 | %MX356.7 - %MX356.0 | %MB356 | %MW178 | %MD89 | %MW356.X07 - %MW356.X0 | %MW178 | %MD178
357 |  | %MX357.7 - %MX357.0 | %MB357 |  |  | %MW357.X15 - %MW357.X8
358 | 40180 | %MX358.7 - %MX358.0 | %MB358 | %MW179 |  | %MW358.X07 - %MW358.X0 | %MW179
359 |  | %MX359.7 - %MX359.0 | %MB359 |  |  | %MW359.X15 - %MW359.X8
360 | 40181 | %MX360.7 - %MX360.0 | %MB360 | %MW180 | %MD90 | %MW360.X07 - %MW360.X0 | %MW180 | %MD180
361 |  | %MX361.7 - %MX361.0 | %MB361 |  |  | %MW361.X15 - %MW361.X8
362 | 40182 | %MX362.7 - %MX362.0 | %MB362 | %MW181 |  | %MW362.X07 - %MW362.X0 | %MW181
363 |  | %MX363.7 - %MX363.0 | %MB363 |  |  | %MW363.X15 - %MW363.X8
364 | 40183 | %MX364.7 - %MX364.0 | %MB364 | %MW182 | %MD91 | %MW364.X07 - %MW364.X0 | %MW182 | %MD182
365 |  | %MX365.7 - %MX365.0 | %MB365 |  |  | %MW365.X15 - %MW365.X8
366 | 40184 | %MX366.7 - %MX366.0 | %MB366 | %MW183 |  | %MW366.X07 - %MW366.X0 | %MW183
367 |  | %MX367.7 - %MX367.0 | %MB367 |  |  | %MW367.X15 - %MW367.X8
368 | 40185 | %MX368.7 - %MX368.0 | %MB368 | %MW184 | %MD92 | %MW368.X07 - %MW368.X0 | %MW184 | %MD184
369 |  | %MX369.7 - %MX369.0 | %MB369 |  |  | %MW369.X15 - %MW369.X8
370 | 40186 | %MX370.7 - %MX370.0 | %MB370 | %MW185 |  | %MW370.X07 - %MW370.X0 | %MW185
371 |  | %MX371.7 - %MX371.0 | %MB371 |  |  | %MW371.X15 - %MW371.X8
372 | 40187 | %MX372.7 - %MX372.0 | %MB372 | %MW186 | %MD93 | %MW372.X07 - %MW372.X0 | %MW186 | %MD186
373 |  | %MX373.7 - %MX373.0 | %MB373 |  |  | %MW373.X15 - %MW373.X8
374 | 40188 | %MX374.7 - %MX374.0 | %MB374 | %MW187 |  | %MW374.X07 - %MW374.X0 | %MW187
375 |  | %MX375.7 - %MX375.0 | %MB375 |  |  | %MW375.X15 - %MW375.X8
376 | 40189 | %MX376.7 - %MX376.0 | %MB376 | %MW188 | %MD94 | %MW376.X07 - %MW376.X0 | %MW188 | %MD188
377 |  | %MX377.7 - %MX377.0 | %MB377 |  |  | %MW377.X15 - %MW377.X8
378 | 40190 | %MX378.7 - %MX378.0 | %MB378 | %MW189 |  | %MW378.X07 - %MW378.X0 | %MW189
379 |  | %MX379.7 - %MX379.0 | %MB379 |  |  | %MW379.X15 - %MW379.X8
380 | 40191 | %MX380.7 - %MX380.0 | %MB380 | %MW190 | %MD95 | %MW380.X07 - %MW380.X0 | %MW190 | %MD190
381 |  | %MX381.7 - %MX381.0 | %MB381 |  |  | %MW381.X15 - %MW381.X8
382 | 40192 | %MX382.7 - %MX382.0 | %MB382 | %MW191 |  | %MW382.X07 - %MW382.X0 | %MW191
383 |  | %MX383.7 - %MX383.0 | %MB383 |  |  | %MW383.X15 - %MW383.X8
384 | 40193 | %MX384.7 - %MX384.0 | %MB384 | %MW192 | %MD96 | %MW384.X07 - %MW384.X0 | %MW192 | %MD192
385 |  | %MX385.7 - %MX385.0 | %MB385 |  |  | %MW385.X15 - %MW385.X8
386 | 40194 | %MX386.7 - %MX386.0 | %MB386 | %MW193 |  | %MW386.X07 - %MW386.X0 | %MW193
387 |  | %MX387.7 - %MX387.0 | %MB387 |  |  | %MW387.X15 - %MW387.X8
388 | 40195 | %MX388.7 - %MX388.0 | %MB388 | %MW194 | %MD97 | %MW388.X07 - %MW388.X0 | %MW194 | %MD194
389 |  | %MX389.7 - %MX389.0 | %MB389 |  |  | %MW389.X15 - %MW389.X8
390 | 40196 | %MX390.7 - %MX390.0 | %MB390 | %MW195 |  | %MW390.X07 - %MW390.X0 | %MW195
391 |  | %MX391.7 - %MX391.0 | %MB391 |  |  | %MW391.X15 - %MW391.X8
392 | 40197 | %MX392.7 - %MX392.0 | %MB392 | %MW196 | %MD98 | %MW392.X07 - %MW392.X0 | %MW196 | %MD196
393 |  | %MX393.7 - %MX393.0 | %MB393 |  |  | %MW393.X15 - %MW393.X8
394 | 40198 | %MX394.7 - %MX394.0 | %MB394 | %MW197 |  | %MW394.X07 - %MW394.X0 | %MW197
395 |  | %MX395.7 - %MX395.0 | %MB395 |  |  | %MW395.X15 - %MW395.X8
396 | 40199 | %MX396.7 - %MX396.0 | %MB396 | %MW198 | %MD99 | %MW396.X07 - %MW396.X0 | %MW198 | %MD198
397 |  | %MX397.7 - %MX397.0 | %MB397 |  |  | %MW397.X15 - %MW397.X8
398 | 40200 | %MX398.7 - %MX398.0 | %MB398 | %MW199 |  | %MW398.X07 - %MW398.X0 | %MW199
399 |  | %MX399.7 - %MX399.0 | %MB399 |  |  | %MW399.X15 - %MW399.X8
400 | 40201 | %MX400.7 - %MX400.0 | %MB400 | %MW200 | %MD100 | %MW400.X07 - %MW400.X0 | %MW200 | %MD200
401 |  | %MX401.7 - %MX401.0 | %MB401 |  |  | %MW401.X15 - %MW401.X8
402 | 40202 | %MX402.7 - %MX402.0 | %MB402 | %MW201 |  | %MW402.X07 - %MW402.X0 | %MW201
403 |  | %MX403.7 - %MX403.0 | %MB403 |  |  | %MW403.X15 - %MW403.X8
404 | 40203 | %MX404.7 - %MX404.0 | %MB404 | %MW202 | %MD101 | %MW404.X07 - %MW404.X0 | %MW202 | %MD202
405 |  | %MX405.7 - %MX405.0 | %MB405 |  |  | %MW405.X15 - %MW405.X8
406 | 40204 | %MX406.7 - %MX406.0 | %MB406 | %MW203 |  | %MW406.X07 - %MW406.X0 | %MW203
407 |  | %MX407.7 - %MX407.0 | %MB407 |  |  | %MW407.X15 - %MW407.X8
408 | 40205 | %MX408.7 - %MX408.0 | %MB408 | %MW204 | %MD102 | %MW408.X07 - %MW408.X0 | %MW204 | %MD204
409 |  | %MX409.7 - %MX409.0 | %MB409 |  |  | %MW409.X15 - %MW409.X8
410 | 40206 | %MX410.7 - %MX410.0 | %MB410 | %MW205 |  | %MW410.X07 - %MW410.X0 | %MW205
411 |  | %MX411.7 - %MX411.0 | %MB411 |  |  | %MW411.X15 - %MW411.X8
412 | 40207 | %MX412.7 - %MX412.0 | %MB412 | %MW206 | %MD103 | %MW412.X07 - %MW412.X0 | %MW206 | %MD206
413 |  | %MX413.7 - %MX413.0 | %MB413 |  |  | %MW413.X15 - %MW413.X8
414 | 40208 | %MX414.7 - %MX414.0 | %MB414 | %MW207 |  | %MW414.X07 - %MW414.X0 | %MW207
415 |  | %MX415.7 - %MX415.0 | %MB415 |  |  | %MW415.X15 - %MW415.X8
416 | 40209 | %MX416.7 - %MX416.0 | %MB416 | %MW208 | %MD104 | %MW416.X07 - %MW416.X0 | %MW208 | %MD208
417 |  | %MX417.7 - %MX417.0 | %MB417 |  |  | %MW417.X15 - %MW417.X8
418 | 40210 | %MX418.7 - %MX418.0 | %MB418 | %MW209 |  | %MW418.X07 - %MW418.X0 | %MW209
419 |  | %MX419.7 - %MX419.0 | %MB419 |  |  | %MW419.X15 - %MW419.X8
420 | 40211 | %MX420.7 - %MX420.0 | %MB420 | %MW210 | %MD105 | %MW420.X07 - %MW420.X0 | %MW210 | %MD210
421 |  | %MX421.7 - %MX421.0 | %MB421 |  |  | %MW421.X15 - %MW421.X8
422 | 40212 | %MX422.7 - %MX422.0 | %MB422 | %MW211 |  | %MW422.X07 - %MW422.X0 | %MW211
423 |  | %MX423.7 - %MX423.0 | %MB423 |  |  | %MW423.X15 - %MW423.X8
424 | 40213 | %MX424.7 - %MX424.0 | %MB424 | %MW212 | %MD106 | %MW424.X07 - %MW424.X0 | %MW212 | %MD212
425 |  | %MX425.7 - %MX425.0 | %MB425 |  |  | %MW425.X15 - %MW425.X8
426 | 40214 | %MX426.7 - %MX426.0 | %MB426 | %MW213 |  | %MW426.X07 - %MW426.X0 | %MW213
427 |  | %MX427.7 - %MX427.0 | %MB427 |  |  | %MW427.X15 - %MW427.X8
428 | 40215 | %MX428.7 - %MX428.0 | %MB428 | %MW214 | %MD107 | %MW428.X07 - %MW428.X0 | %MW214 | %MD214
429 |  | %MX429.7 - %MX429.0 | %MB429 |  |  | %MW429.X15 - %MW429.X8
430 | 40216 | %MX430.7 - %MX430.0 | %MB430 | %MW215 |  | %MW430.X07 - %MW430.X0 | %MW215
431 |  | %MX431.7 - %MX431.0 | %MB431 |  |  | %MW431.X15 - %MW431.X8
432 | 40217 | %MX432.7 - %MX432.0 | %MB432 | %MW216 | %MD108 | %MW432.X07 - %MW432.X0 | %MW216 | %MD216
433 |  | %MX433.7 - %MX433.0 | %MB433 |  |  | %MW433.X15 - %MW433.X8
434 | 40218 | %MX434.7 - %MX434.0 | %MB434 | %MW217 |  | %MW434.X07 - %MW434.X0 | %MW217
435 |  | %MX435.7 - %MX435.0 | %MB435 |  |  | %MW435.X15 - %MW435.X8
436 | 40219 | %MX436.7 - %MX436.0 | %MB436 | %MW218 | %MD109 | %MW436.X07 - %MW436.X0 | %MW218 | %MD218
437 |  | %MX437.7 - %MX437.0 | %MB437 |  |  | %MW437.X15 - %MW437.X8
438 | 40220 | %MX438.7 - %MX438.0 | %MB438 | %MW219 |  | %MW438.X07 - %MW438.X0 | %MW219
439 |  | %MX439.7 - %MX439.0 | %MB439 |  |  | %MW439.X15 - %MW439.X8
440 | 40221 | %MX440.7 - %MX440.0 | %MB440 | %MW220 | %MD110 | %MW440.X07 - %MW440.X0 | %MW220 | %MD220
441 |  | %MX441.7 - %MX441.0 | %MB441 |  |  | %MW441.X15 - %MW441.X8
442 | 40222 | %MX442.7 - %MX442.0 | %MB442 | %MW221 |  | %MW442.X07 - %MW442.X0 | %MW221
443 |  | %MX443.7 - %MX443.0 | %MB443 |  |  | %MW443.X15 - %MW443.X8
444 | 40223 | %MX444.7 - %MX444.0 | %MB444 | %MW222 | %MD111 | %MW444.X07 - %MW444.X0 | %MW222 | %MD222
445 |  | %MX445.7 - %MX445.0 | %MB445 |  |  | %MW445.X15 - %MW445.X8
446 | 40224 | %MX446.7 - %MX446.0 | %MB446 | %MW223 |  | %MW446.X07 - %MW446.X0 | %MW223
447 |  | %MX447.7 - %MX447.0 | %MB447 |  |  | %MW447.X15 - %MW447.X8
448 | 40225 | %MX448.7 - %MX448.0 | %MB448 | %MW224 | %MD112 | %MW448.X07 - %MW448.X0 | %MW224 | %MD224
449 |  | %MX449.7 - %MX449.0 | %MB449 |  |  | %MW449.X15 - %MW449.X8
450 | 40226 | %MX450.7 - %MX450.0 | %MB450 | %MW225 |  | %MW450.X07 - %MW450.X0 | %MW225
451 |  | %MX451.7 - %MX451.0 | %MB451 |  |  | %MW451.X15 - %MW451.X8
452 | 40227 | %MX452.7 - %MX452.0 | %MB452 | %MW226 | %MD113 | %MW452.X07 - %MW452.X0 | %MW226 | %MD226
453 |  | %MX453.7 - %MX453.0 | %MB453 |  |  | %MW453.X15 - %MW453.X8
454 | 40228 | %MX454.7 - %MX454.0 | %MB454 | %MW227 |  | %MW454.X07 - %MW454.X0 | %MW227
455 |  | %MX455.7 - %MX455.0 | %MB455 |  |  | %MW455.X15 - %MW455.X8
456 | 40229 | %MX456.7 - %MX456.0 | %MB456 | %MW228 | %MD114 | %MW456.X07 - %MW456.X0 | %MW228 | %MD228
457 |  | %MX457.7 - %MX457.0 | %MB457 |  |  | %MW457.X15 - %MW457.X8
458 | 40230 | %MX458.7 - %MX458.0 | %MB458 | %MW229 |  | %MW458.X07 - %MW458.X0 | %MW229
459 |  | %MX459.7 - %MX459.0 | %MB459 |  |  | %MW459.X15 - %MW459.X8
460 | 40231 | %MX460.7 - %MX460.0 | %MB460 | %MW230 | %MD115 | %MW460.X07 - %MW460.X0 | %MW230 | %MD230
461 |  | %MX461.7 - %MX461.0 | %MB461 |  |  | %MW461.X15 - %MW461.X8
462 | 40232 | %MX462.7 - %MX462.0 | %MB462 | %MW231 |  | %MW462.X07 - %MW462.X0 | %MW231
463 |  | %MX463.7 - %MX463.0 | %MB463 |  |  | %MW463.X15 - %MW463.X8
464 | 40233 | %MX464.7 - %MX464.0 | %MB464 | %MW232 | %MD116 | %MW464.X07 - %MW464.X0 | %MW232 | %MD232
465 |  | %MX465.7 - %MX465.0 | %MB465 |  |  | %MW465.X15 - %MW465.X8
466 | 40234 | %MX466.7 - %MX466.0 | %MB466 | %MW233 |  | %MW466.X07 - %MW466.X0 | %MW233
467 |  | %MX467.7 - %MX467.0 | %MB467 |  |  | %MW467.X15 - %MW467.X8
468 | 40235 | %MX468.7 - %MX468.0 | %MB468 | %MW234 | %MD117 | %MW468.X07 - %MW468.X0 | %MW234 | %MD234
469 |  | %MX469.7 - %MX469.0 | %MB469 |  |  | %MW469.X15 - %MW469.X8
470 | 40236 | %MX470.7 - %MX470.0 | %MB470 | %MW235 |  | %MW470.X07 - %MW470.X0 | %MW235
471 |  | %MX471.7 - %MX471.0 | %MB471 |  |  | %MW471.X15 - %MW471.X8
472 | 40237 | %MX472.7 - %MX472.0 | %MB472 | %MW236 | %MD118 | %MW472.X07 - %MW472.X0 | %MW236 | %MD236
473 |  | %MX473.7 - %MX473.0 | %MB473 |  |  | %MW473.X15 - %MW473.X8
474 | 40238 | %MX474.7 - %MX474.0 | %MB474 | %MW237 |  | %MW474.X07 - %MW474.X0 | %MW237
475 |  | %MX475.7 - %MX475.0 | %MB475 |  |  | %MW475.X15 - %MW475.X8
476 | 40239 | %MX476.7 - %MX476.0 | %MB476 | %MW238 | %MD119 | %MW476.X07 - %MW476.X0 | %MW238 | %MD238
477 |  | %MX477.7 - %MX477.0 | %MB477 |  |  | %MW477.X15 - %MW477.X8
478 | 40240 | %MX478.7 - %MX478.0 | %MB478 | %MW239 |  | %MW478.X07 - %MW478.X0 | %MW239
479 |  | %MX479.7 - %MX479.0 | %MB479 |  |  | %MW479.X15 - %MW479.X8
480 | 40241 | %MX480.7 - %MX480.0 | %MB480 | %MW240 | %MD120 | %MW480.X07 - %MW480.X0 | %MW240 | %MD240
481 |  | %MX481.7 - %MX481.0 | %MB481 |  |  | %MW481.X15 - %MW481.X8
482 | 40242 | %MX482.7 - %MX482.0 | %MB482 | %MW241 |  | %MW482.X07 - %MW482.X0 | %MW241
483 |  | %MX483.7 - %MX483.0 | %MB483 |  |  | %MW483.X15 - %MW483.X8
484 | 40243 | %MX484.7 - %MX484.0 | %MB484 | %MW242 | %MD121 | %MW484.X07 - %MW484.X0 | %MW242 | %MD242
485 |  | %MX485.7 - %MX485.0 | %MB485 |  |  | %MW485.X15 - %MW485.X8
486 | 40244 | %MX486.7 - %MX486.0 | %MB486 | %MW243 |  | %MW486.X07 - %MW486.X0 | %MW243
487 |  | %MX487.7 - %MX487.0 | %MB487 |  |  | %MW487.X15 - %MW487.X8
488 | 40245 | %MX488.7 - %MX488.0 | %MB488 | %MW244 | %MD122 | %MW488.X07 - %MW488.X0 | %MW244 | %MD244
489 |  | %MX489.7 - %MX489.0 | %MB489 |  |  | %MW489.X15 - %MW489.X8
490 | 40246 | %MX490.7 - %MX490.0 | %MB490 | %MW245 |  | %MW490.X07 - %MW490.X0 | %MW245
491 |  | %MX491.7 - %MX491.0 | %MB491 |  |  | %MW491.X15 - %MW491.X8
492 | 40247 | %MX492.7 - %MX492.0 | %MB492 | %MW246 | %MD123 | %MW492.X07 - %MW492.X0 | %MW246 | %MD246
493 |  | %MX493.7 - %MX493.0 | %MB493 |  |  | %MW493.X15 - %MW493.X8
494 | 40248 | %MX494.7 - %MX494.0 | %MB494 | %MW247 |  | %MW494.X07 - %MW494.X0 | %MW247
495 |  | %MX495.7 - %MX495.0 | %MB495 |  |  | %MW495.X15 - %MW495.X8
496 | 40249 | %MX496.7 - %MX496.0 | %MB496 | %MW248 | %MD124 | %MW496.X07 - %MW496.X0 | %MW248 | %MD248
497 |  | %MX497.7 - %MX497.0 | %MB497 |  |  | %MW497.X15 - %MW497.X8
498 | 40250 | %MX498.7 - %MX498.0 | %MB498 | %MW249 |  | %MW498.X07 - %MW498.X0 | %MW249
499 |  | %MX499.7 - %MX499.0 | %MB499 |  |  | %MW499.X15 - %MW499.X8
500 | 40251 | %MX500.7 - %MX500.0 | %MB500 | %MW250 | %MD125 | %MW500.X07 - %MW500.X0 | %MW250 | %MD250
501 |  | %MX501.7 - %MX501.0 | %MB501 |  |  | %MW501.X15 - %MW501.X8
502 | 40252 | %MX502.7 - %MX502.0 | %MB502 | %MW251 |  | %MW502.X07 - %MW502.X0 | %MW251
503 |  | %MX503.7 - %MX503.0 | %MB503 |  |  | %MW503.X15 - %MW503.X8
504 | 40253 | %MX504.7 - %MX504.0 | %MB504 | %MW252 | %MD126 | %MW504.X07 - %MW504.X0 | %MW252 | %MD252
505 |  | %MX505.7 - %MX505.0 | %MB505 |  |  | %MW505.X15 - %MW505.X8
506 | 40254 | %MX506.7 - %MX506.0 | %MB506 | %MW253 |  | %MW506.X07 - %MW506.X0 | %MW253
507 |  | %MX507.7 - %MX507.0 | %MB507 |  |  | %MW507.X15 - %MW507.X8
508 | 40255 | %MX508.7 - %MX508.0 | %MB508 | %MW254 | %MD127 | %MW508.X07 - %MW508.X0 | %MW254 | %MD254
509 |  | %MX509.7 - %MX509.0 | %MB509 |  |  | %MW509.X15 - %MW509.X8
510 | 40256 | %MX510.7 - %MX510.0 | %MB510 | %MW255 |  | %MW510.X07 - %MW510.X0 | %MW255
511 |  | %MX511.7 - %MX511.0 | %MB511 |  |  | %MW511.X15 - %MW511.X8
512 | 40257 | %MX512.7 - %MX512.0 | %MB512 | %MW256 | %MD128 | %MW512.X07 - %MW512.X0 | %MW256 | %MD256
513 |  | %MX513.7 - %MX513.0 | %MB513 |  |  | %MW513.X15 - %MW513.X8
514 | 40258 | %MX514.7 - %MX514.0 | %MB514 | %MW257 |  | %MW514.X07 - %MW514.X0 | %MW257
515 |  | %MX515.7 - %MX515.0 | %MB515 |  |  | %MW515.X15 - %MW515.X8
516 | 40259 | %MX516.7 - %MX516.0 | %MB516 | %MW258 | %MD129 | %MW516.X07 - %MW516.X0 | %MW258 | %MD258
517 |  | %MX517.7 - %MX517.0 | %MB517 |  |  | %MW517.X15 - %MW517.X8
518 | 40260 | %MX518.7 - %MX518.0 | %MB518 | %MW259 |  | %MW518.X07 - %MW518.X0 | %MW259
519 |  | %MX519.7 - %MX519.0 | %MB519 |  |  | %MW519.X15 - %MW519.X8
520 | 40261 | %MX520.7 - %MX520.0 | %MB520 | %MW260 | %MD130 | %MW520.X07 - %MW520.X0 | %MW260 | %MD260
521 |  | %MX521.7 - %MX521.0 | %MB521 |  |  | %MW521.X15 - %MW521.X8
522 | 40262 | %MX522.7 - %MX522.0 | %MB522 | %MW261 |  | %MW522.X07 - %MW522.X0 | %MW261
523 |  | %MX523.7 - %MX523.0 | %MB523 |  |  | %MW523.X15 - %MW523.X8
524 | 40263 | %MX524.7 - %MX524.0 | %MB524 | %MW262 | %MD131 | %MW524.X07 - %MW524.X0 | %MW262 | %MD262
525 |  | %MX525.7 - %MX525.0 | %MB525 |  |  | %MW525.X15 - %MW525.X8
526 | 40264 | %MX526.7 - %MX526.0 | %MB526 | %MW263 |  | %MW526.X07 - %MW526.X0 | %MW263
527 |  | %MX527.7 - %MX527.0 | %MB527 |  |  | %MW527.X15 - %MW527.X8
528 | 40265 | %MX528.7 - %MX528.0 | %MB528 | %MW264 | %MD132 | %MW528.X07 - %MW528.X0 | %MW264 | %MD264
529 |  | %MX529.7 - %MX529.0 | %MB529 |  |  | %MW529.X15 - %MW529.X8
530 | 40266 | %MX530.7 - %MX530.0 | %MB530 | %MW265 |  | %MW530.X07 - %MW530.X0 | %MW265
531 |  | %MX531.7 - %MX531.0 | %MB531 |  |  | %MW531.X15 - %MW531.X8
532 | 40267 | %MX532.7 - %MX532.0 | %MB532 | %MW266 | %MD133 | %MW532.X07 - %MW532.X0 | %MW266 | %MD266
533 |  | %MX533.7 - %MX533.0 | %MB533 |  |  | %MW533.X15 - %MW533.X8
534 | 40268 | %MX534.7 - %MX534.0 | %MB534 | %MW267 |  | %MW534.X07 - %MW534.X0 | %MW267
535 |  | %MX535.7 - %MX535.0 | %MB535 |  |  | %MW535.X15 - %MW535.X8
536 | 40269 | %MX536.7 - %MX536.0 | %MB536 | %MW268 | %MD134 | %MW536.X07 - %MW536.X0 | %MW268 | %MD268
537 |  | %MX537.7 - %MX537.0 | %MB537 |  |  | %MW537.X15 - %MW537.X8
538 | 40270 | %MX538.7 - %MX538.0 | %MB538 | %MW269 |  | %MW538.X07 - %MW538.X0 | %MW269
539 |  | %MX539.7 - %MX539.0 | %MB539 |  |  | %MW539.X15 - %MW539.X8
540 | 40271 | %MX540.7 - %MX540.0 | %MB540 | %MW270 | %MD135 | %MW540.X07 - %MW540.X0 | %MW270 | %MD270
541 |  | %MX541.7 - %MX541.0 | %MB541 |  |  | %MW541.X15 - %MW541.X8
542 | 40272 | %MX542.7 - %MX542.0 | %MB542 | %MW271 |  | %MW542.X07 - %MW542.X0 | %MW271
543 |  | %MX543.7 - %MX543.0 | %MB543 |  |  | %MW543.X15 - %MW543.X8
544 | 40273 | %MX544.7 - %MX544.0 | %MB544 | %MW272 | %MD136 | %MW544.X07 - %MW544.X0 | %MW272 | %MD272
545 |  | %MX545.7 - %MX545.0 | %MB545 |  |  | %MW545.X15 - %MW545.X8
546 | 40274 | %MX546.7 - %MX546.0 | %MB546 | %MW273 |  | %MW546.X07 - %MW546.X0 | %MW273
547 |  | %MX547.7 - %MX547.0 | %MB547 |  |  | %MW547.X15 - %MW547.X8
548 | 40275 | %MX548.7 - %MX548.0 | %MB548 | %MW274 | %MD137 | %MW548.X07 - %MW548.X0 | %MW274 | %MD274
549 |  | %MX549.7 - %MX549.0 | %MB549 |  |  | %MW549.X15 - %MW549.X8
550 | 40276 | %MX550.7 - %MX550.0 | %MB550 | %MW275 |  | %MW550.X07 - %MW550.X0 | %MW275
551 |  | %MX551.7 - %MX551.0 | %MB551 |  |  | %MW551.X15 - %MW551.X8
552 | 40277 | %MX552.7 - %MX552.0 | %MB552 | %MW276 | %MD138 | %MW552.X07 - %MW552.X0 | %MW276 | %MD276
553 |  | %MX553.7 - %MX553.0 | %MB553 |  |  | %MW553.X15 - %MW553.X8
554 | 40278 | %MX554.7 - %MX554.0 | %MB554 | %MW277 |  | %MW554.X07 - %MW554.X0 | %MW277
555 |  | %MX555.7 - %MX555.0 | %MB555 |  |  | %MW555.X15 - %MW555.X8
556 | 40279 | %MX556.7 - %MX556.0 | %MB556 | %MW278 | %MD139 | %MW556.X07 - %MW556.X0 | %MW278 | %MD278
557 |  | %MX557.7 - %MX557.0 | %MB557 |  |  | %MW557.X15 - %MW557.X8
558 | 40280 | %MX558.7 - %MX558.0 | %MB558 | %MW279 |  | %MW558.X07 - %MW558.X0 | %MW279
559 |  | %MX559.7 - %MX559.0 | %MB559 |  |  | %MW559.X15 - %MW559.X8
560 | 40281 | %MX560.7 - %MX560.0 | %MB560 | %MW280 | %MD140 | %MW560.X07 - %MW560.X0 | %MW280 | %MD280
561 |  | %MX561.7 - %MX561.0 | %MB561 |  |  | %MW561.X15 - %MW561.X8
562 | 40282 | %MX562.7 - %MX562.0 | %MB562 | %MW281 |  | %MW562.X07 - %MW562.X0 | %MW281
563 |  | %MX563.7 - %MX563.0 | %MB563 |  |  | %MW563.X15 - %MW563.X8
564 | 40283 | %MX564.7 - %MX564.0 | %MB564 | %MW282 | %MD141 | %MW564.X07 - %MW564.X0 | %MW282 | %MD282
565 |  | %MX565.7 - %MX565.0 | %MB565 |  |  | %MW565.X15 - %MW565.X8
566 | 40284 | %MX566.7 - %MX566.0 | %MB566 | %MW283 |  | %MW566.X07 - %MW566.X0 | %MW283
567 |  | %MX567.7 - %MX567.0 | %MB567 |  |  | %MW567.X15 - %MW567.X8
568 | 40285 | %MX568.7 - %MX568.0 | %MB568 | %MW284 | %MD142 | %MW568.X07 - %MW568.X0 | %MW284 | %MD284
569 |  | %MX569.7 - %MX569.0 | %MB569 |  |  | %MW569.X15 - %MW569.X8
570 | 40286 | %MX570.7 - %MX570.0 | %MB570 | %MW285 |  | %MW570.X07 - %MW570.X0 | %MW285
571 |  | %MX571.7 - %MX571.0 | %MB571 |  |  | %MW571.X15 - %MW571.X8
572 | 40287 | %MX572.7 - %MX572.0 | %MB572 | %MW286 | %MD143 | %MW572.X07 - %MW572.X0 | %MW286 | %MD286
573 |  | %MX573.7 - %MX573.0 | %MB573 |  |  | %MW573.X15 - %MW573.X8
574 | 40288 | %MX574.7 - %MX574.0 | %MB574 | %MW287 |  | %MW574.X07 - %MW574.X0 | %MW287
575 |  | %MX575.7 - %MX575.0 | %MB575 |  |  | %MW575.X15 - %MW575.X8
576 | 40289 | %MX576.7 - %MX576.0 | %MB576 | %MW288 | %MD144 | %MW576.X07 - %MW576.X0 | %MW288 | %MD288
577 |  | %MX577.7 - %MX577.0 | %MB577 |  |  | %MW577.X15 - %MW577.X8
578 | 40290 | %MX578.7 - %MX578.0 | %MB578 | %MW289 |  | %MW578.X07 - %MW578.X0 | %MW289
579 |  | %MX579.7 - %MX579.0 | %MB579 |  |  | %MW579.X15 - %MW579.X8
580 | 40291 | %MX580.7 - %MX580.0 | %MB580 | %MW290 | %MD145 | %MW580.X07 - %MW580.X0 | %MW290 | %MD290
581 |  | %MX581.7 - %MX581.0 | %MB581 |  |  | %MW581.X15 - %MW581.X8
582 | 40292 | %MX582.7 - %MX582.0 | %MB582 | %MW291 |  | %MW582.X07 - %MW582.X0 | %MW291
583 |  | %MX583.7 - %MX583.0 | %MB583 |  |  | %MW583.X15 - %MW583.X8
584 | 40293 | %MX584.7 - %MX584.0 | %MB584 | %MW292 | %MD146 | %MW584.X07 - %MW584.X0 | %MW292 | %MD292
585 |  | %MX585.7 - %MX585.0 | %MB585 |  |  | %MW585.X15 - %MW585.X8
586 | 40294 | %MX586.7 - %MX586.0 | %MB586 | %MW293 |  | %MW586.X07 - %MW586.X0 | %MW293
587 |  | %MX587.7 - %MX587.0 | %MB587 |  |  | %MW587.X15 - %MW587.X8
588 | 40295 | %MX588.7 - %MX588.0 | %MB588 | %MW294 | %MD147 | %MW588.X07 - %MW588.X0 | %MW294 | %MD294
589 |  | %MX589.7 - %MX589.0 | %MB589 |  |  | %MW589.X15 - %MW589.X8
590 | 40296 | %MX590.7 - %MX590.0 | %MB590 | %MW295 |  | %MW590.X07 - %MW590.X0 | %MW295
591 |  | %MX591.7 - %MX591.0 | %MB591 |  |  | %MW591.X15 - %MW591.X8
592 | 40297 | %MX592.7 - %MX592.0 | %MB592 | %MW296 | %MD148 | %MW592.X07 - %MW592.X0 | %MW296 | %MD296
593 |  | %MX593.7 - %MX593.0 | %MB593 |  |  | %MW593.X15 - %MW593.X8
594 | 40298 | %MX594.7 - %MX594.0 | %MB594 | %MW297 |  | %MW594.X07 - %MW594.X0 | %MW297
595 |  | %MX595.7 - %MX595.0 | %MB595 |  |  | %MW595.X15 - %MW595.X8
596 | 40299 | %MX596.7 - %MX596.0 | %MB596 | %MW298 | %MD149 | %MW596.X07 - %MW596.X0 | %MW298 | %MD298
597 |  | %MX597.7 - %MX597.0 | %MB597 |  |  | %MW597.X15 - %MW597.X8
598 | 40300 | %MX598.7 - %MX598.0 | %MB598 | %MW299 |  | %MW598.X07 - %MW598.X0 | %MW299
599 |  | %MX599.7 - %MX599.0 | %MB599 |  |  | %MW599.X15 - %MW599.X8
600 | 40301 | %MX600.7 - %MX600.0 | %MB600 | %MW300 | %MD150 | %MW600.X07 - %MW600.X0 | %MW300 | %MD300
601 |  | %MX601.7 - %MX601.0 | %MB601 |  |  | %MW601.X15 - %MW601.X8
602 | 40302 | %MX602.7 - %MX602.0 | %MB602 | %MW301 |  | %MW602.X07 - %MW602.X0 | %MW301
603 |  | %MX603.7 - %MX603.0 | %MB603 |  |  | %MW603.X15 - %MW603.X8
604 | 40303 | %MX604.7 - %MX604.0 | %MB604 | %MW302 | %MD151 | %MW604.X07 - %MW604.X0 | %MW302 | %MD302
605 |  | %MX605.7 - %MX605.0 | %MB605 |  |  | %MW605.X15 - %MW605.X8
606 | 40304 | %MX606.7 - %MX606.0 | %MB606 | %MW303 |  | %MW606.X07 - %MW606.X0 | %MW303
607 |  | %MX607.7 - %MX607.0 | %MB607 |  |  | %MW607.X15 - %MW607.X8
608 | 40305 | %MX608.7 - %MX608.0 | %MB608 | %MW304 | %MD152 | %MW608.X07 - %MW608.X0 | %MW304 | %MD304
609 |  | %MX609.7 - %MX609.0 | %MB609 |  |  | %MW609.X15 - %MW609.X8
610 | 40306 | %MX610.7 - %MX610.0 | %MB610 | %MW305 |  | %MW610.X07 - %MW610.X0 | %MW305
611 |  | %MX611.7 - %MX611.0 | %MB611 |  |  | %MW611.X15 - %MW611.X8
612 | 40307 | %MX612.7 - %MX612.0 | %MB612 | %MW306 | %MD153 | %MW612.X07 - %MW612.X0 | %MW306 | %MD306
613 |  | %MX613.7 - %MX613.0 | %MB613 |  |  | %MW613.X15 - %MW613.X8
614 | 40308 | %MX614.7 - %MX614.0 | %MB614 | %MW307 |  | %MW614.X07 - %MW614.X0 | %MW307
615 |  | %MX615.7 - %MX615.0 | %MB615 |  |  | %MW615.X15 - %MW615.X8
616 | 40309 | %MX616.7 - %MX616.0 | %MB616 | %MW308 | %MD154 | %MW616.X07 - %MW616.X0 | %MW308 | %MD308
617 |  | %MX617.7 - %MX617.0 | %MB617 |  |  | %MW617.X15 - %MW617.X8
618 | 40310 | %MX618.7 - %MX618.0 | %MB618 | %MW309 |  | %MW618.X07 - %MW618.X0 | %MW309
619 |  | %MX619.7 - %MX619.0 | %MB619 |  |  | %MW619.X15 - %MW619.X8
620 | 40311 | %MX620.7 - %MX620.0 | %MB620 | %MW310 | %MD155 | %MW620.X07 - %MW620.X0 | %MW310 | %MD310
621 |  | %MX621.7 - %MX621.0 | %MB621 |  |  | %MW621.X15 - %MW621.X8
622 | 40312 | %MX622.7 - %MX622.0 | %MB622 | %MW311 |  | %MW622.X07 - %MW622.X0 | %MW311
623 |  | %MX623.7 - %MX623.0 | %MB623 |  |  | %MW623.X15 - %MW623.X8
624 | 40313 | %MX624.7 - %MX624.0 | %MB624 | %MW312 | %MD156 | %MW624.X07 - %MW624.X0 | %MW312 | %MD312
625 |  | %MX625.7 - %MX625.0 | %MB625 |  |  | %MW625.X15 - %MW625.X8
626 | 40314 | %MX626.7 - %MX626.0 | %MB626 | %MW313 |  | %MW626.X07 - %MW626.X0 | %MW313
627 |  | %MX627.7 - %MX627.0 | %MB627 |  |  | %MW627.X15 - %MW627.X8
628 | 40315 | %MX628.7 - %MX628.0 | %MB628 | %MW314 | %MD157 | %MW628.X07 - %MW628.X0 | %MW314 | %MD314
629 |  | %MX629.7 - %MX629.0 | %MB629 |  |  | %MW629.X15 - %MW629.X8
630 | 40316 | %MX630.7 - %MX630.0 | %MB630 | %MW315 |  | %MW630.X07 - %MW630.X0 | %MW315
631 |  | %MX631.7 - %MX631.0 | %MB631 |  |  | %MW631.X15 - %MW631.X8
632 | 40317 | %MX632.7 - %MX632.0 | %MB632 | %MW316 | %MD158 | %MW632.X07 - %MW632.X0 | %MW316 | %MD316
633 |  | %MX633.7 - %MX633.0 | %MB633 |  |  | %MW633.X15 - %MW633.X8
634 | 40318 | %MX634.7 - %MX634.0 | %MB634 | %MW317 |  | %MW634.X07 - %MW634.X0 | %MW317
635 |  | %MX635.7 - %MX635.0 | %MB635 |  |  | %MW635.X15 - %MW635.X8
636 | 40319 | %MX636.7 - %MX636.0 | %MB636 | %MW318 | %MD159 | %MW636.X07 - %MW636.X0 | %MW318 | %MD318
637 |  | %MX637.7 - %MX637.0 | %MB637 |  |  | %MW637.X15 - %MW637.X8
638 | 40320 | %MX638.7 - %MX638.0 | %MB638 | %MW319 |  | %MW638.X07 - %MW638.X0 | %MW319
639 |  | %MX639.7 - %MX639.0 | %MB639 |  |  | %MW639.X15 - %MW639.X8
640 | 40321 | %MX640.7 - %MX640.0 | %MB640 | %MW320 | %MD160 | %MW640.X07 - %MW640.X0 | %MW320 | %MD320
641 |  | %MX641.7 - %MX641.0 | %MB641 |  |  | %MW641.X15 - %MW641.X8
642 | 40322 | %MX642.7 - %MX642.0 | %MB642 | %MW321 |  | %MW642.X07 - %MW642.X0 | %MW321
643 |  | %MX643.7 - %MX643.0 | %MB643 |  |  | %MW643.X15 - %MW643.X8
644 | 40323 | %MX644.7 - %MX644.0 | %MB644 | %MW322 | %MD161 | %MW644.X07 - %MW644.X0 | %MW322 | %MD322
645 |  | %MX645.7 - %MX645.0 | %MB645 |  |  | %MW645.X15 - %MW645.X8
646 | 40324 | %MX646.7 - %MX646.0 | %MB646 | %MW323 |  | %MW646.X07 - %MW646.X0 | %MW323
647 |  | %MX647.7 - %MX647.0 | %MB647 |  |  | %MW647.X15 - %MW647.X8
648 | 40325 | %MX648.7 - %MX648.0 | %MB648 | %MW324 | %MD162 | %MW648.X07 - %MW648.X0 | %MW324 | %MD324
649 |  | %MX649.7 - %MX649.0 | %MB649 |  |  | %MW649.X15 - %MW649.X8
650 | 40326 | %MX650.7 - %MX650.0 | %MB650 | %MW325 |  | %MW650.X07 - %MW650.X0 | %MW325
651 |  | %MX651.7 - %MX651.0 | %MB651 |  |  | %MW651.X15 - %MW651.X8
652 | 40327 | %MX652.7 - %MX652.0 | %MB652 | %MW326 | %MD163 | %MW652.X07 - %MW652.X0 | %MW326 | %MD326
653 |  | %MX653.7 - %MX653.0 | %MB653 |  |  | %MW653.X15 - %MW653.X8
654 | 40328 | %MX654.7 - %MX654.0 | %MB654 | %MW327 |  | %MW654.X07 - %MW654.X0 | %MW327
655 |  | %MX655.7 - %MX655.0 | %MB655 |  |  | %MW655.X15 - %MW655.X8
656 | 40329 | %MX656.7 - %MX656.0 | %MB656 | %MW328 | %MD164 | %MW656.X07 - %MW656.X0 | %MW328 | %MD328
657 |  | %MX657.7 - %MX657.0 | %MB657 |  |  | %MW657.X15 - %MW657.X8
658 | 40330 | %MX658.7 - %MX658.0 | %MB658 | %MW329 |  | %MW658.X07 - %MW658.X0 | %MW329
659 |  | %MX659.7 - %MX659.0 | %MB659 |  |  | %MW659.X15 - %MW659.X8
660 | 40331 | %MX660.7 - %MX660.0 | %MB660 | %MW330 | %MD165 | %MW660.X07 - %MW660.X0 | %MW330 | %MD330
661 |  | %MX661.7 - %MX661.0 | %MB661 |  |  | %MW661.X15 - %MW661.X8
662 | 40332 | %MX662.7 - %MX662.0 | %MB662 | %MW331 |  | %MW662.X07 - %MW662.X0 | %MW331
663 |  | %MX663.7 - %MX663.0 | %MB663 |  |  | %MW663.X15 - %MW663.X8
664 | 40333 | %MX664.7 - %MX664.0 | %MB664 | %MW332 | %MD166 | %MW664.X07 - %MW664.X0 | %MW332 | %MD332
665 |  | %MX665.7 - %MX665.0 | %MB665 |  |  | %MW665.X15 - %MW665.X8
666 | 40334 | %MX666.7 - %MX666.0 | %MB666 | %MW333 |  | %MW666.X07 - %MW666.X0 | %MW333
667 |  | %MX667.7 - %MX667.0 | %MB667 |  |  | %MW667.X15 - %MW667.X8
668 | 40335 | %MX668.7 - %MX668.0 | %MB668 | %MW334 | %MD167 | %MW668.X07 - %MW668.X0 | %MW334 | %MD334
669 |  | %MX669.7 - %MX669.0 | %MB669 |  |  | %MW669.X15 - %MW669.X8
670 | 40336 | %MX670.7 - %MX670.0 | %MB670 | %MW335 |  | %MW670.X07 - %MW670.X0 | %MW335
671 |  | %MX671.7 - %MX671.0 | %MB671 |  |  | %MW671.X15 - %MW671.X8
672 | 40337 | %MX672.7 - %MX672.0 | %MB672 | %MW336 | %MD168 | %MW672.X07 - %MW672.X0 | %MW336 | %MD336
673 |  | %MX673.7 - %MX673.0 | %MB673 |  |  | %MW673.X15 - %MW673.X8
674 | 40338 | %MX674.7 - %MX674.0 | %MB674 | %MW337 |  | %MW674.X07 - %MW674.X0 | %MW337
675 |  | %MX675.7 - %MX675.0 | %MB675 |  |  | %MW675.X15 - %MW675.X8
676 | 40339 | %MX676.7 - %MX676.0 | %MB676 | %MW338 | %MD169 | %MW676.X07 - %MW676.X0 | %MW338 | %MD338
677 |  | %MX677.7 - %MX677.0 | %MB677 |  |  | %MW677.X15 - %MW677.X8
678 | 40340 | %MX678.7 - %MX678.0 | %MB678 | %MW339 |  | %MW678.X07 - %MW678.X0 | %MW339
679 |  | %MX679.7 - %MX679.0 | %MB679 |  |  | %MW679.X15 - %MW679.X8
680 | 40341 | %MX680.7 - %MX680.0 | %MB680 | %MW340 | %MD170 | %MW680.X07 - %MW680.X0 | %MW340 | %MD340
681 |  | %MX681.7 - %MX681.0 | %MB681 |  |  | %MW681.X15 - %MW681.X8
682 | 40342 | %MX682.7 - %MX682.0 | %MB682 | %MW341 |  | %MW682.X07 - %MW682.X0 | %MW341
683 |  | %MX683.7 - %MX683.0 | %MB683 |  |  | %MW683.X15 - %MW683.X8
684 | 40343 | %MX684.7 - %MX684.0 | %MB684 | %MW342 | %MD171 | %MW684.X07 - %MW684.X0 | %MW342 | %MD342
685 |  | %MX685.7 - %MX685.0 | %MB685 |  |  | %MW685.X15 - %MW685.X8
686 | 40344 | %MX686.7 - %MX686.0 | %MB686 | %MW343 |  | %MW686.X07 - %MW686.X0 | %MW343
687 |  | %MX687.7 - %MX687.0 | %MB687 |  |  | %MW687.X15 - %MW687.X8
688 | 40345 | %MX688.7 - %MX688.0 | %MB688 | %MW344 | %MD172 | %MW688.X07 - %MW688.X0 | %MW344 | %MD344
689 |  | %MX689.7 - %MX689.0 | %MB689 |  |  | %MW689.X15 - %MW689.X8
690 | 40346 | %MX690.7 - %MX690.0 | %MB690 | %MW345 |  | %MW690.X07 - %MW690.X0 | %MW345
691 |  | %MX691.7 - %MX691.0 | %MB691 |  |  | %MW691.X15 - %MW691.X8
692 | 40347 | %MX692.7 - %MX692.0 | %MB692 | %MW346 | %MD173 | %MW692.X07 - %MW692.X0 | %MW346 | %MD346
693 |  | %MX693.7 - %MX693.0 | %MB693 |  |  | %MW693.X15 - %MW693.X8
694 | 40348 | %MX694.7 - %MX694.0 | %MB694 | %MW347 |  | %MW694.X07 - %MW694.X0 | %MW347
695 |  | %MX695.7 - %MX695.0 | %MB695 |  |  | %MW695.X15 - %MW695.X8
696 | 40349 | %MX696.7 - %MX696.0 | %MB696 | %MW348 | %MD174 | %MW696.X07 - %MW696.X0 | %MW348 | %MD348
697 |  | %MX697.7 - %MX697.0 | %MB697 |  |  | %MW697.X15 - %MW697.X8
698 | 40350 | %MX698.7 - %MX698.0 | %MB698 | %MW349 |  | %MW698.X07 - %MW698.X0 | %MW349
699 |  | %MX699.7 - %MX699.0 | %MB699 |  |  | %MW699.X15 - %MW699.X8
700 | 40351 | %MX700.7 - %MX700.0 | %MB700 | %MW350 | %MD175 | %MW700.X07 - %MW700.X0 | %MW350 | %MD350
701 |  | %MX701.7 - %MX701.0 | %MB701 |  |  | %MW701.X15 - %MW701.X8
702 | 40352 | %MX702.7 - %MX702.0 | %MB702 | %MW351 |  | %MW702.X07 - %MW702.X0 | %MW351
703 |  | %MX703.7 - %MX703.0 | %MB703 |  |  | %MW703.X15 - %MW703.X8
704 | 40353 | %MX704.7 - %MX704.0 | %MB704 | %MW352 | %MD176 | %MW704.X07 - %MW704.X0 | %MW352 | %MD352
705 |  | %MX705.7 - %MX705.0 | %MB705 |  |  | %MW705.X15 - %MW705.X8
706 | 40354 | %MX706.7 - %MX706.0 | %MB706 | %MW353 |  | %MW706.X07 - %MW706.X0 | %MW353
707 |  | %MX707.7 - %MX707.0 | %MB707 |  |  | %MW707.X15 - %MW707.X8
708 | 40355 | %MX708.7 - %MX708.0 | %MB708 | %MW354 | %MD177 | %MW708.X07 - %MW708.X0 | %MW354 | %MD354
709 |  | %MX709.7 - %MX709.0 | %MB709 |  |  | %MW709.X15 - %MW709.X8
710 | 40356 | %MX710.7 - %MX710.0 | %MB710 | %MW355 |  | %MW710.X07 - %MW710.X0 | %MW355
711 |  | %MX711.7 - %MX711.0 | %MB711 |  |  | %MW711.X15 - %MW711.X8
712 | 40357 | %MX712.7 - %MX712.0 | %MB712 | %MW356 | %MD178 | %MW712.X07 - %MW712.X0 | %MW356 | %MD356
713 |  | %MX713.7 - %MX713.0 | %MB713 |  |  | %MW713.X15 - %MW713.X8
714 | 40358 | %MX714.7 - %MX714.0 | %MB714 | %MW357 |  | %MW714.X07 - %MW714.X0 | %MW357
715 |  | %MX715.7 - %MX715.0 | %MB715 |  |  | %MW715.X15 - %MW715.X8
716 | 40359 | %MX716.7 - %MX716.0 | %MB716 | %MW358 | %MD179 | %MW716.X07 - %MW716.X0 | %MW358 | %MD358
717 |  | %MX717.7 - %MX717.0 | %MB717 |  |  | %MW717.X15 - %MW717.X8
718 | 40360 | %MX718.7 - %MX718.0 | %MB718 | %MW359 |  | %MW718.X07 - %MW718.X0 | %MW359
719 |  | %MX719.7 - %MX719.0 | %MB719 |  |  | %MW719.X15 - %MW719.X8
720 | 40361 | %MX720.7 - %MX720.0 | %MB720 | %MW360 | %MD180 | %MW720.X07 - %MW720.X0 | %MW360 | %MD360
721 |  | %MX721.7 - %MX721.0 | %MB721 |  |  | %MW721.X15 - %MW721.X8
722 | 40362 | %MX722.7 - %MX722.0 | %MB722 | %MW361 |  | %MW722.X07 - %MW722.X0 | %MW361
723 |  | %MX723.7 - %MX723.0 | %MB723 |  |  | %MW723.X15 - %MW723.X8
724 | 40363 | %MX724.7 - %MX724.0 | %MB724 | %MW362 | %MD181 | %MW724.X07 - %MW724.X0 | %MW362 | %MD362
725 |  | %MX725.7 - %MX725.0 | %MB725 |  |  | %MW725.X15 - %MW725.X8
726 | 40364 | %MX726.7 - %MX726.0 | %MB726 | %MW363 |  | %MW726.X07 - %MW726.X0 | %MW363
727 |  | %MX727.7 - %MX727.0 | %MB727 |  |  | %MW727.X15 - %MW727.X8
728 | 40365 | %MX728.7 - %MX728.0 | %MB728 | %MW364 | %MD182 | %MW728.X07 - %MW728.X0 | %MW364 | %MD364
729 |  | %MX729.7 - %MX729.0 | %MB729 |  |  | %MW729.X15 - %MW729.X8
730 | 40366 | %MX730.7 - %MX730.0 | %MB730 | %MW365 |  | %MW730.X07 - %MW730.X0 | %MW365
731 |  | %MX731.7 - %MX731.0 | %MB731 |  |  | %MW731.X15 - %MW731.X8
732 | 40367 | %MX732.7 - %MX732.0 | %MB732 | %MW366 | %MD183 | %MW732.X07 - %MW732.X0 | %MW366 | %MD366
733 |  | %MX733.7 - %MX733.0 | %MB733 |  |  | %MW733.X15 - %MW733.X8
734 | 40368 | %MX734.7 - %MX734.0 | %MB734 | %MW367 |  | %MW734.X07 - %MW734.X0 | %MW367
735 |  | %MX735.7 - %MX735.0 | %MB735 |  |  | %MW735.X15 - %MW735.X8
736 | 40369 | %MX736.7 - %MX736.0 | %MB736 | %MW368 | %MD184 | %MW736.X07 - %MW736.X0 | %MW368 | %MD368
737 |  | %MX737.7 - %MX737.0 | %MB737 |  |  | %MW737.X15 - %MW737.X8
738 | 40370 | %MX738.7 - %MX738.0 | %MB738 | %MW369 |  | %MW738.X07 - %MW738.X0 | %MW369
739 |  | %MX739.7 - %MX739.0 | %MB739 |  |  | %MW739.X15 - %MW739.X8
740 | 40371 | %MX740.7 - %MX740.0 | %MB740 | %MW370 | %MD185 | %MW740.X07 - %MW740.X0 | %MW370 | %MD370
741 |  | %MX741.7 - %MX741.0 | %MB741 |  |  | %MW741.X15 - %MW741.X8
742 | 40372 | %MX742.7 - %MX742.0 | %MB742 | %MW371 |  | %MW742.X07 - %MW742.X0 | %MW371
743 |  | %MX743.7 - %MX743.0 | %MB743 |  |  | %MW743.X15 - %MW743.X8
744 | 40373 | %MX744.7 - %MX744.0 | %MB744 | %MW372 | %MD186 | %MW744.X07 - %MW744.X0 | %MW372 | %MD372
745 |  | %MX745.7 - %MX745.0 | %MB745 |  |  | %MW745.X15 - %MW745.X8
746 | 40374 | %MX746.7 - %MX746.0 | %MB746 | %MW373 |  | %MW746.X07 - %MW746.X0 | %MW373
747 |  | %MX747.7 - %MX747.0 | %MB747 |  |  | %MW747.X15 - %MW747.X8
748 | 40375 | %MX748.7 - %MX748.0 | %MB748 | %MW374 | %MD187 | %MW748.X07 - %MW748.X0 | %MW374 | %MD374
749 |  | %MX749.7 - %MX749.0 | %MB749 |  |  | %MW749.X15 - %MW749.X8
750 | 40376 | %MX750.7 - %MX750.0 | %MB750 | %MW375 |  | %MW750.X07 - %MW750.X0 | %MW375
751 |  | %MX751.7 - %MX751.0 | %MB751 |  |  | %MW751.X15 - %MW751.X8
752 | 40377 | %MX752.7 - %MX752.0 | %MB752 | %MW376 | %MD188 | %MW752.X07 - %MW752.X0 | %MW376 | %MD376
753 |  | %MX753.7 - %MX753.0 | %MB753 |  |  | %MW753.X15 - %MW753.X8
754 | 40378 | %MX754.7 - %MX754.0 | %MB754 | %MW377 |  | %MW754.X07 - %MW754.X0 | %MW377
755 |  | %MX755.7 - %MX755.0 | %MB755 |  |  | %MW755.X15 - %MW755.X8
756 | 40379 | %MX756.7 - %MX756.0 | %MB756 | %MW378 | %MD189 | %MW756.X07 - %MW756.X0 | %MW378 | %MD378
757 |  | %MX757.7 - %MX757.0 | %MB757 |  |  | %MW757.X15 - %MW757.X8
758 | 40380 | %MX758.7 - %MX758.0 | %MB758 | %MW379 |  | %MW758.X07 - %MW758.X0 | %MW379
759 |  | %MX759.7 - %MX759.0 | %MB759 |  |  | %MW759.X15 - %MW759.X8
760 | 40381 | %MX760.7 - %MX760.0 | %MB760 | %MW380 | %MD190 | %MW760.X07 - %MW760.X0 | %MW380 | %MD380
761 |  | %MX761.7 - %MX761.0 | %MB761 |  |  | %MW761.X15 - %MW761.X8
762 | 40382 | %MX762.7 - %MX762.0 | %MB762 | %MW381 |  | %MW762.X07 - %MW762.X0 | %MW381
763 |  | %MX763.7 - %MX763.0 | %MB763 |  |  | %MW763.X15 - %MW763.X8
764 | 40383 | %MX764.7 - %MX764.0 | %MB764 | %MW382 | %MD191 | %MW764.X07 - %MW764.X0 | %MW382 | %MD382
765 |  | %MX765.7 - %MX765.0 | %MB765 |  |  | %MW765.X15 - %MW765.X8
766 | 40384 | %MX766.7 - %MX766.0 | %MB766 | %MW383 |  | %MW766.X07 - %MW766.X0 | %MW383
767 |  | %MX767.7 - %MX767.0 | %MB767 |  |  | %MW767.X15 - %MW767.X8
768 | 40385 | %MX768.7 - %MX768.0 | %MB768 | %MW384 | %MD192 | %MW768.X07 - %MW768.X0 | %MW384 | %MD384
769 |  | %MX769.7 - %MX769.0 | %MB769 |  |  | %MW769.X15 - %MW769.X8
770 | 40386 | %MX770.7 - %MX770.0 | %MB770 | %MW385 |  | %MW770.X07 - %MW770.X0 | %MW385
771 |  | %MX771.7 - %MX771.0 | %MB771 |  |  | %MW771.X15 - %MW771.X8
772 | 40387 | %MX772.7 - %MX772.0 | %MB772 | %MW386 | %MD193 | %MW772.X07 - %MW772.X0 | %MW386 | %MD386
773 |  | %MX773.7 - %MX773.0 | %MB773 |  |  | %MW773.X15 - %MW773.X8
774 | 40388 | %MX774.7 - %MX774.0 | %MB774 | %MW387 |  | %MW774.X07 - %MW774.X0 | %MW387
775 |  | %MX775.7 - %MX775.0 | %MB775 |  |  | %MW775.X15 - %MW775.X8
776 | 40389 | %MX776.7 - %MX776.0 | %MB776 | %MW388 | %MD194 | %MW776.X07 - %MW776.X0 | %MW388 | %MD388
777 |  | %MX777.7 - %MX777.0 | %MB777 |  |  | %MW777.X15 - %MW777.X8
778 | 40390 | %MX778.7 - %MX778.0 | %MB778 | %MW389 |  | %MW778.X07 - %MW778.X0 | %MW389
779 |  | %MX779.7 - %MX779.0 | %MB779 |  |  | %MW779.X15 - %MW779.X8
780 | 40391 | %MX780.7 - %MX780.0 | %MB780 | %MW390 | %MD195 | %MW780.X07 - %MW780.X0 | %MW390 | %MD390
781 |  | %MX781.7 - %MX781.0 | %MB781 |  |  | %MW781.X15 - %MW781.X8
782 | 40392 | %MX782.7 - %MX782.0 | %MB782 | %MW391 |  | %MW782.X07 - %MW782.X0 | %MW391
783 |  | %MX783.7 - %MX783.0 | %MB783 |  |  | %MW783.X15 - %MW783.X8
784 | 40393 | %MX784.7 - %MX784.0 | %MB784 | %MW392 | %MD196 | %MW784.X07 - %MW784.X0 | %MW392 | %MD392
785 |  | %MX785.7 - %MX785.0 | %MB785 |  |  | %MW785.X15 - %MW785.X8
786 | 40394 | %MX786.7 - %MX786.0 | %MB786 | %MW393 |  | %MW786.X07 - %MW786.X0 | %MW393
787 |  | %MX787.7 - %MX787.0 | %MB787 |  |  | %MW787.X15 - %MW787.X8
788 | 40395 | %MX788.7 - %MX788.0 | %MB788 | %MW394 | %MD197 | %MW788.X07 - %MW788.X0 | %MW394 | %MD394
789 |  | %MX789.7 - %MX789.0 | %MB789 |  |  | %MW789.X15 - %MW789.X8
790 | 40396 | %MX790.7 - %MX790.0 | %MB790 | %MW395 |  | %MW790.X07 - %MW790.X0 | %MW395
791 |  | %MX791.7 - %MX791.0 | %MB791 |  |  | %MW791.X15 - %MW791.X8
792 | 40397 | %MX792.7 - %MX792.0 | %MB792 | %MW396 | %MD198 | %MW792.X07 - %MW792.X0 | %MW396 | %MD396
793 |  | %MX793.7 - %MX793.0 | %MB793 |  |  | %MW793.X15 - %MW793.X8
794 | 40398 | %MX794.7 - %MX794.0 | %MB794 | %MW397 |  | %MW794.X07 - %MW794.X0 | %MW397
795 |  | %MX795.7 - %MX795.0 | %MB795 |  |  | %MW795.X15 - %MW795.X8
796 | 40399 | %MX796.7 - %MX796.0 | %MB796 | %MW398 | %MD199 | %MW796.X07 - %MW796.X0 | %MW398 | %MD398
797 |  | %MX797.7 - %MX797.0 | %MB797 |  |  | %MW797.X15 - %MW797.X8
798 | 40400 | %MX798.7 - %MX798.0 | %MB798 | %MW399 |  | %MW798.X07 - %MW798.X0 | %MW399
799 |  | %MX799.7 - %MX799.0 | %MB799 |  |  | %MW799.X15 - %MW799.X8
800 | 40401 | %MX800.7 - %MX800.0 | %MB800 | %MW400 | %MD200 | %MW800.X07 - %MW800.X0 | %MW400 | %MD400
801 |  | %MX801.7 - %MX801.0 | %MB801 |  |  | %MW801.X15 - %MW801.X8
802 | 40402 | %MX802.7 - %MX802.0 | %MB802 | %MW401 |  | %MW802.X07 - %MW802.X0 | %MW401
803 |  | %MX803.7 - %MX803.0 | %MB803 |  |  | %MW803.X15 - %MW803.X8
804 | 40403 | %MX804.7 - %MX804.0 | %MB804 | %MW402 | %MD201 | %MW804.X07 - %MW804.X0 | %MW402 | %MD402
805 |  | %MX805.7 - %MX805.0 | %MB805 |  |  | %MW805.X15 - %MW805.X8
806 | 40404 | %MX806.7 - %MX806.0 | %MB806 | %MW403 |  | %MW806.X07 - %MW806.X0 | %MW403
807 |  | %MX807.7 - %MX807.0 | %MB807 |  |  | %MW807.X15 - %MW807.X8
808 | 40405 | %MX808.7 - %MX808.0 | %MB808 | %MW404 | %MD202 | %MW808.X07 - %MW808.X0 | %MW404 | %MD404
809 |  | %MX809.7 - %MX809.0 | %MB809 |  |  | %MW809.X15 - %MW809.X8
810 | 40406 | %MX810.7 - %MX810.0 | %MB810 | %MW405 |  | %MW810.X07 - %MW810.X0 | %MW405
811 |  | %MX811.7 - %MX811.0 | %MB811 |  |  | %MW811.X15 - %MW811.X8
812 | 40407 | %MX812.7 - %MX812.0 | %MB812 | %MW406 | %MD203 | %MW812.X07 - %MW812.X0 | %MW406 | %MD406
813 |  | %MX813.7 - %MX813.0 | %MB813 |  |  | %MW813.X15 - %MW813.X8
814 | 40408 | %MX814.7 - %MX814.0 | %MB814 | %MW407 |  | %MW814.X07 - %MW814.X0 | %MW407
815 |  | %MX815.7 - %MX815.0 | %MB815 |  |  | %MW815.X15 - %MW815.X8
816 | 40409 | %MX816.7 - %MX816.0 | %MB816 | %MW408 | %MD204 | %MW816.X07 - %MW816.X0 | %MW408 | %MD408
817 |  | %MX817.7 - %MX817.0 | %MB817 |  |  | %MW817.X15 - %MW817.X8
818 | 40410 | %MX818.7 - %MX818.0 | %MB818 | %MW409 |  | %MW818.X07 - %MW818.X0 | %MW409
819 |  | %MX819.7 - %MX819.0 | %MB819 |  |  | %MW819.X15 - %MW819.X8
820 | 40411 | %MX820.7 - %MX820.0 | %MB820 | %MW410 | %MD205 | %MW820.X07 - %MW820.X0 | %MW410 | %MD410
821 |  | %MX821.7 - %MX821.0 | %MB821 |  |  | %MW821.X15 - %MW821.X8
822 | 40412 | %MX822.7 - %MX822.0 | %MB822 | %MW411 |  | %MW822.X07 - %MW822.X0 | %MW411
823 |  | %MX823.7 - %MX823.0 | %MB823 |  |  | %MW823.X15 - %MW823.X8
824 | 40413 | %MX824.7 - %MX824.0 | %MB824 | %MW412 | %MD206 | %MW824.X07 - %MW824.X0 | %MW412 | %MD412
825 |  | %MX825.7 - %MX825.0 | %MB825 |  |  | %MW825.X15 - %MW825.X8
826 | 40414 | %MX826.7 - %MX826.0 | %MB826 | %MW413 |  | %MW826.X07 - %MW826.X0 | %MW413
827 |  | %MX827.7 - %MX827.0 | %MB827 |  |  | %MW827.X15 - %MW827.X8
828 | 40415 | %MX828.7 - %MX828.0 | %MB828 | %MW414 | %MD207 | %MW828.X07 - %MW828.X0 | %MW414 | %MD414
829 |  | %MX829.7 - %MX829.0 | %MB829 |  |  | %MW829.X15 - %MW829.X8
830 | 40416 | %MX830.7 - %MX830.0 | %MB830 | %MW415 |  | %MW830.X07 - %MW830.X0 | %MW415
831 |  | %MX831.7 - %MX831.0 | %MB831 |  |  | %MW831.X15 - %MW831.X8
832 | 40417 | %MX832.7 - %MX832.0 | %MB832 | %MW416 | %MD208 | %MW832.X07 - %MW832.X0 | %MW416 | %MD416
833 |  | %MX833.7 - %MX833.0 | %MB833 |  |  | %MW833.X15 - %MW833.X8
834 | 40418 | %MX834.7 - %MX834.0 | %MB834 | %MW417 |  | %MW834.X07 - %MW834.X0 | %MW417
835 |  | %MX835.7 - %MX835.0 | %MB835 |  |  | %MW835.X15 - %MW835.X8
836 | 40419 | %MX836.7 - %MX836.0 | %MB836 | %MW418 | %MD209 | %MW836.X07 - %MW836.X0 | %MW418 | %MD418
837 |  | %MX837.7 - %MX837.0 | %MB837 |  |  | %MW837.X15 - %MW837.X8
838 | 40420 | %MX838.7 - %MX838.0 | %MB838 | %MW419 |  | %MW838.X07 - %MW838.X0 | %MW419
839 |  | %MX839.7 - %MX839.0 | %MB839 |  |  | %MW839.X15 - %MW839.X8
840 | 40421 | %MX840.7 - %MX840.0 | %MB840 | %MW420 | %MD210 | %MW840.X07 - %MW840.X0 | %MW420 | %MD420
841 |  | %MX841.7 - %MX841.0 | %MB841 |  |  | %MW841.X15 - %MW841.X8
842 | 40422 | %MX842.7 - %MX842.0 | %MB842 | %MW421 |  | %MW842.X07 - %MW842.X0 | %MW421
843 |  | %MX843.7 - %MX843.0 | %MB843 |  |  | %MW843.X15 - %MW843.X8
844 | 40423 | %MX844.7 - %MX844.0 | %MB844 | %MW422 | %MD211 | %MW844.X07 - %MW844.X0 | %MW422 | %MD422
845 |  | %MX845.7 - %MX845.0 | %MB845 |  |  | %MW845.X15 - %MW845.X8
846 | 40424 | %MX846.7 - %MX846.0 | %MB846 | %MW423 |  | %MW846.X07 - %MW846.X0 | %MW423
847 |  | %MX847.7 - %MX847.0 | %MB847 |  |  | %MW847.X15 - %MW847.X8
848 | 40425 | %MX848.7 - %MX848.0 | %MB848 | %MW424 | %MD212 | %MW848.X07 - %MW848.X0 | %MW424 | %MD424
849 |  | %MX849.7 - %MX849.0 | %MB849 |  |  | %MW849.X15 - %MW849.X8
850 | 40426 | %MX850.7 - %MX850.0 | %MB850 | %MW425 |  | %MW850.X07 - %MW850.X0 | %MW425
851 |  | %MX851.7 - %MX851.0 | %MB851 |  |  | %MW851.X15 - %MW851.X8
852 | 40427 | %MX852.7 - %MX852.0 | %MB852 | %MW426 | %MD213 | %MW852.X07 - %MW852.X0 | %MW426 | %MD426
853 |  | %MX853.7 - %MX853.0 | %MB853 |  |  | %MW853.X15 - %MW853.X8
854 | 40428 | %MX854.7 - %MX854.0 | %MB854 | %MW427 |  | %MW854.X07 - %MW854.X0 | %MW427
855 |  | %MX855.7 - %MX855.0 | %MB855 |  |  | %MW855.X15 - %MW855.X8
856 | 40429 | %MX856.7 - %MX856.0 | %MB856 | %MW428 | %MD214 | %MW856.X07 - %MW856.X0 | %MW428 | %MD428
857 |  | %MX857.7 - %MX857.0 | %MB857 |  |  | %MW857.X15 - %MW857.X8
858 | 40430 | %MX858.7 - %MX858.0 | %MB858 | %MW429 |  | %MW858.X07 - %MW858.X0 | %MW429
859 |  | %MX859.7 - %MX859.0 | %MB859 |  |  | %MW859.X15 - %MW859.X8
860 | 40431 | %MX860.7 - %MX860.0 | %MB860 | %MW430 | %MD215 | %MW860.X07 - %MW860.X0 | %MW430 | %MD430
861 |  | %MX861.7 - %MX861.0 | %MB861 |  |  | %MW861.X15 - %MW861.X8
862 | 40432 | %MX862.7 - %MX862.0 | %MB862 | %MW431 |  | %MW862.X07 - %MW862.X0 | %MW431
863 |  | %MX863.7 - %MX863.0 | %MB863 |  |  | %MW863.X15 - %MW863.X8
864 | 40433 | %MX864.7 - %MX864.0 | %MB864 | %MW432 | %MD216 | %MW864.X07 - %MW864.X0 | %MW432 | %MD432
865 |  | %MX865.7 - %MX865.0 | %MB865 |  |  | %MW865.X15 - %MW865.X8
866 | 40434 | %MX866.7 - %MX866.0 | %MB866 | %MW433 |  | %MW866.X07 - %MW866.X0 | %MW433
867 |  | %MX867.7 - %MX867.0 | %MB867 |  |  | %MW867.X15 - %MW867.X8
868 | 40435 | %MX868.7 - %MX868.0 | %MB868 | %MW434 | %MD217 | %MW868.X07 - %MW868.X0 | %MW434 | %MD434
869 |  | %MX869.7 - %MX869.0 | %MB869 |  |  | %MW869.X15 - %MW869.X8
870 | 40436 | %MX870.7 - %MX870.0 | %MB870 | %MW435 |  | %MW870.X07 - %MW870.X0 | %MW435
871 |  | %MX871.7 - %MX871.0 | %MB871 |  |  | %MW871.X15 - %MW871.X8
872 | 40437 | %MX872.7 - %MX872.0 | %MB872 | %MW436 | %MD218 | %MW872.X07 - %MW872.X0 | %MW436 | %MD436
873 |  | %MX873.7 - %MX873.0 | %MB873 |  |  | %MW873.X15 - %MW873.X8
874 | 40438 | %MX874.7 - %MX874.0 | %MB874 | %MW437 |  | %MW874.X07 - %MW874.X0 | %MW437
875 |  | %MX875.7 - %MX875.0 | %MB875 |  |  | %MW875.X15 - %MW875.X8
876 | 40439 | %MX876.7 - %MX876.0 | %MB876 | %MW438 | %MD219 | %MW876.X07 - %MW876.X0 | %MW438 | %MD438
877 |  | %MX877.7 - %MX877.0 | %MB877 |  |  | %MW877.X15 - %MW877.X8
878 | 40440 | %MX878.7 - %MX878.0 | %MB878 | %MW439 |  | %MW878.X07 - %MW878.X0 | %MW439
879 |  | %MX879.7 - %MX879.0 | %MB879 |  |  | %MW879.X15 - %MW879.X8
880 | 40441 | %MX880.7 - %MX880.0 | %MB880 | %MW440 | %MD220 | %MW880.X07 - %MW880.X0 | %MW440 | %MD440
881 |  | %MX881.7 - %MX881.0 | %MB881 |  |  | %MW881.X15 - %MW881.X8
882 | 40442 | %MX882.7 - %MX882.0 | %MB882 | %MW441 |  | %MW882.X07 - %MW882.X0 | %MW441
883 |  | %MX883.7 - %MX883.0 | %MB883 |  |  | %MW883.X15 - %MW883.X8
884 | 40443 | %MX884.7 - %MX884.0 | %MB884 | %MW442 | %MD221 | %MW884.X07 - %MW884.X0 | %MW442 | %MD442
885 |  | %MX885.7 - %MX885.0 | %MB885 |  |  | %MW885.X15 - %MW885.X8
886 | 40444 | %MX886.7 - %MX886.0 | %MB886 | %MW443 |  | %MW886.X07 - %MW886.X0 | %MW443
887 |  | %MX887.7 - %MX887.0 | %MB887 |  |  | %MW887.X15 - %MW887.X8
888 | 40445 | %MX888.7 - %MX888.0 | %MB888 | %MW444 | %MD222 | %MW888.X07 - %MW888.X0 | %MW444 | %MD444
889 |  | %MX889.7 - %MX889.0 | %MB889 |  |  | %MW889.X15 - %MW889.X8
890 | 40446 | %MX890.7 - %MX890.0 | %MB890 | %MW445 |  | %MW890.X07 - %MW890.X0 | %MW445
891 |  | %MX891.7 - %MX891.0 | %MB891 |  |  | %MW891.X15 - %MW891.X8
892 | 40447 | %MX892.7 - %MX892.0 | %MB892 | %MW446 | %MD223 | %MW892.X07 - %MW892.X0 | %MW446 | %MD446
893 |  | %MX893.7 - %MX893.0 | %MB893 |  |  | %MW893.X15 - %MW893.X8
894 | 40448 | %MX894.7 - %MX894.0 | %MB894 | %MW447 |  | %MW894.X07 - %MW894.X0 | %MW447
895 |  | %MX895.7 - %MX895.0 | %MB895 |  |  | %MW895.X15 - %MW895.X8
896 | 40449 | %MX896.7 - %MX896.0 | %MB896 | %MW448 | %MD224 | %MW896.X07 - %MW896.X0 | %MW448 | %MD448
897 |  | %MX897.7 - %MX897.0 | %MB897 |  |  | %MW897.X15 - %MW897.X8
898 | 40450 | %MX898.7 - %MX898.0 | %MB898 | %MW449 |  | %MW898.X07 - %MW898.X0 | %MW449
899 |  | %MX899.7 - %MX899.0 | %MB899 |  |  | %MW899.X15 - %MW899.X8
900 | 40451 | %MX900.7 - %MX900.0 | %MB900 | %MW450 | %MD225 | %MW900.X07 - %MW900.X0 | %MW450 | %MD450
901 |  | %MX901.7 - %MX901.0 | %MB901 |  |  | %MW901.X15 - %MW901.X8
902 | 40452 | %MX902.7 - %MX902.0 | %MB902 | %MW451 |  | %MW902.X07 - %MW902.X0 | %MW451
903 |  | %MX903.7 - %MX903.0 | %MB903 |  |  | %MW903.X15 - %MW903.X8
904 | 40453 | %MX904.7 - %MX904.0 | %MB904 | %MW452 | %MD226 | %MW904.X07 - %MW904.X0 | %MW452 | %MD452
905 |  | %MX905.7 - %MX905.0 | %MB905 |  |  | %MW905.X15 - %MW905.X8
906 | 40454 | %MX906.7 - %MX906.0 | %MB906 | %MW453 |  | %MW906.X07 - %MW906.X0 | %MW453
907 |  | %MX907.7 - %MX907.0 | %MB907 |  |  | %MW907.X15 - %MW907.X8
908 | 40455 | %MX908.7 - %MX908.0 | %MB908 | %MW454 | %MD227 | %MW908.X07 - %MW908.X0 | %MW454 | %MD454
909 |  | %MX909.7 - %MX909.0 | %MB909 |  |  | %MW909.X15 - %MW909.X8
910 | 40456 | %MX910.7 - %MX910.0 | %MB910 | %MW455 |  | %MW910.X07 - %MW910.X0 | %MW455
911 |  | %MX911.7 - %MX911.0 | %MB911 |  |  | %MW911.X15 - %MW911.X8
912 | 40457 | %MX912.7 - %MX912.0 | %MB912 | %MW456 | %MD228 | %MW912.X07 - %MW912.X0 | %MW456 | %MD456
913 |  | %MX913.7 - %MX913.0 | %MB913 |  |  | %MW913.X15 - %MW913.X8
914 | 40458 | %MX914.7 - %MX914.0 | %MB914 | %MW457 |  | %MW914.X07 - %MW914.X0 | %MW457
915 |  | %MX915.7 - %MX915.0 | %MB915 |  |  | %MW915.X15 - %MW915.X8
916 | 40459 | %MX916.7 - %MX916.0 | %MB916 | %MW458 | %MD229 | %MW916.X07 - %MW916.X0 | %MW458 | %MD458
917 |  | %MX917.7 - %MX917.0 | %MB917 |  |  | %MW917.X15 - %MW917.X8
918 | 40460 | %MX918.7 - %MX918.0 | %MB918 | %MW459 |  | %MW918.X07 - %MW918.X0 | %MW459
919 |  | %MX919.7 - %MX919.0 | %MB919 |  |  | %MW919.X15 - %MW919.X8
920 | 40461 | %MX920.7 - %MX920.0 | %MB920 | %MW460 | %MD230 | %MW920.X07 - %MW920.X0 | %MW460 | %MD460
921 |  | %MX921.7 - %MX921.0 | %MB921 |  |  | %MW921.X15 - %MW921.X8
922 | 40462 | %MX922.7 - %MX922.0 | %MB922 | %MW461 |  | %MW922.X07 - %MW922.X0 | %MW461
923 |  | %MX923.7 - %MX923.0 | %MB923 |  |  | %MW923.X15 - %MW923.X8
924 | 40463 | %MX924.7 - %MX924.0 | %MB924 | %MW462 | %MD231 | %MW924.X07 - %MW924.X0 | %MW462 | %MD462
925 |  | %MX925.7 - %MX925.0 | %MB925 |  |  | %MW925.X15 - %MW925.X8
926 | 40464 | %MX926.7 - %MX926.0 | %MB926 | %MW463 |  | %MW926.X07 - %MW926.X0 | %MW463
927 |  | %MX927.7 - %MX927.0 | %MB927 |  |  | %MW927.X15 - %MW927.X8
928 | 40465 | %MX928.7 - %MX928.0 | %MB928 | %MW464 | %MD232 | %MW928.X07 - %MW928.X0 | %MW464 | %MD464
929 |  | %MX929.7 - %MX929.0 | %MB929 |  |  | %MW929.X15 - %MW929.X8
930 | 40466 | %MX930.7 - %MX930.0 | %MB930 | %MW465 |  | %MW930.X07 - %MW930.X0 | %MW465
931 |  | %MX931.7 - %MX931.0 | %MB931 |  |  | %MW931.X15 - %MW931.X8
932 | 40467 | %MX932.7 - %MX932.0 | %MB932 | %MW466 | %MD233 | %MW932.X07 - %MW932.X0 | %MW466 | %MD466
933 |  | %MX933.7 - %MX933.0 | %MB933 |  |  | %MW933.X15 - %MW933.X8
934 | 40468 | %MX934.7 - %MX934.0 | %MB934 | %MW467 |  | %MW934.X07 - %MW934.X0 | %MW467
935 |  | %MX935.7 - %MX935.0 | %MB935 |  |  | %MW935.X15 - %MW935.X8
936 | 40469 | %MX936.7 - %MX936.0 | %MB936 | %MW468 | %MD234 | %MW936.X07 - %MW936.X0 | %MW468 | %MD468
937 |  | %MX937.7 - %MX937.0 | %MB937 |  |  | %MW937.X15 - %MW937.X8
938 | 40470 | %MX938.7 - %MX938.0 | %MB938 | %MW469 |  | %MW938.X07 - %MW938.X0 | %MW469
939 |  | %MX939.7 - %MX939.0 | %MB939 |  |  | %MW939.X15 - %MW939.X8
940 | 40471 | %MX940.7 - %MX940.0 | %MB940 | %MW470 | %MD235 | %MW940.X07 - %MW940.X0 | %MW470 | %MD470
941 |  | %MX941.7 - %MX941.0 | %MB941 |  |  | %MW941.X15 - %MW941.X8
942 | 40472 | %MX942.7 - %MX942.0 | %MB942 | %MW471 |  | %MW942.X07 - %MW942.X0 | %MW471
943 |  | %MX943.7 - %MX943.0 | %MB943 |  |  | %MW943.X15 - %MW943.X8
944 | 40473 | %MX944.7 - %MX944.0 | %MB944 | %MW472 | %MD236 | %MW944.X07 - %MW944.X0 | %MW472 | %MD472
945 |  | %MX945.7 - %MX945.0 | %MB945 |  |  | %MW945.X15 - %MW945.X8
946 | 40474 | %MX946.7 - %MX946.0 | %MB946 | %MW473 |  | %MW946.X07 - %MW946.X0 | %MW473
947 |  | %MX947.7 - %MX947.0 | %MB947 |  |  | %MW947.X15 - %MW947.X8
948 | 40475 | %MX948.7 - %MX948.0 | %MB948 | %MW474 | %MD237 | %MW948.X07 - %MW948.X0 | %MW474 | %MD474
949 |  | %MX949.7 - %MX949.0 | %MB949 |  |  | %MW949.X15 - %MW949.X8
950 | 40476 | %MX950.7 - %MX950.0 | %MB950 | %MW475 |  | %MW950.X07 - %MW950.X0 | %MW475
951 |  | %MX951.7 - %MX951.0 | %MB951 |  |  | %MW951.X15 - %MW951.X8
952 | 40477 | %MX952.7 - %MX952.0 | %MB952 | %MW476 | %MD238 | %MW952.X07 - %MW952.X0 | %MW476 | %MD476
953 |  | %MX953.7 - %MX953.0 | %MB953 |  |  | %MW953.X15 - %MW953.X8
954 | 40478 | %MX954.7 - %MX954.0 | %MB954 | %MW477 |  | %MW954.X07 - %MW954.X0 | %MW477
955 |  | %MX955.7 - %MX955.0 | %MB955 |  |  | %MW955.X15 - %MW955.X8
956 | 40479 | %MX956.7 - %MX956.0 | %MB956 | %MW478 | %MD239 | %MW956.X07 - %MW956.X0 | %MW478 | %MD478
957 |  | %MX957.7 - %MX957.0 | %MB957 |  |  | %MW957.X15 - %MW957.X8
958 | 40480 | %MX958.7 - %MX958.0 | %MB958 | %MW479 |  | %MW958.X07 - %MW958.X0 | %MW479
959 |  | %MX959.7 - %MX959.0 | %MB959 |  |  | %MW959.X15 - %MW959.X8
960 | 40481 | %MX960.7 - %MX960.0 | %MB960 | %MW480 | %MD240 | %MW960.X07 - %MW960.X0 | %MW480 | %MD480
961 |  | %MX961.7 - %MX961.0 | %MB961 |  |  | %MW961.X15 - %MW961.X8
962 | 40482 | %MX962.7 - %MX962.0 | %MB962 | %MW481 |  | %MW962.X07 - %MW962.X0 | %MW481
963 |  | %MX963.7 - %MX963.0 | %MB963 |  |  | %MW963.X15 - %MW963.X8
964 | 40483 | %MX964.7 - %MX964.0 | %MB964 | %MW482 | %MD241 | %MW964.X07 - %MW964.X0 | %MW482 | %MD482
965 |  | %MX965.7 - %MX965.0 | %MB965 |  |  | %MW965.X15 - %MW965.X8
966 | 40484 | %MX966.7 - %MX966.0 | %MB966 | %MW483 |  | %MW966.X07 - %MW966.X0 | %MW483
967 |  | %MX967.7 - %MX967.0 | %MB967 |  |  | %MW967.X15 - %MW967.X8
968 | 40485 | %MX968.7 - %MX968.0 | %MB968 | %MW484 | %MD242 | %MW968.X07 - %MW968.X0 | %MW484 | %MD484
969 |  | %MX969.7 - %MX969.0 | %MB969 |  |  | %MW969.X15 - %MW969.X8
970 | 40486 | %MX970.7 - %MX970.0 | %MB970 | %MW485 |  | %MW970.X07 - %MW970.X0 | %MW485
971 |  | %MX971.7 - %MX971.0 | %MB971 |  |  | %MW971.X15 - %MW971.X8
972 | 40487 | %MX972.7 - %MX972.0 | %MB972 | %MW486 | %MD243 | %MW972.X07 - %MW972.X0 | %MW486 | %MD486
973 |  | %MX973.7 - %MX973.0 | %MB973 |  |  | %MW973.X15 - %MW973.X8
974 | 40488 | %MX974.7 - %MX974.0 | %MB974 | %MW487 |  | %MW974.X07 - %MW974.X0 | %MW487
975 |  | %MX975.7 - %MX975.0 | %MB975 |  |  | %MW975.X15 - %MW975.X8
976 | 40489 | %MX976.7 - %MX976.0 | %MB976 | %MW488 | %MD244 | %MW976.X07 - %MW976.X0 | %MW488 | %MD488
977 |  | %MX977.7 - %MX977.0 | %MB977 |  |  | %MW977.X15 - %MW977.X8
978 | 40490 | %MX978.7 - %MX978.0 | %MB978 | %MW489 |  | %MW978.X07 - %MW978.X0 | %MW489
979 |  | %MX979.7 - %MX979.0 | %MB979 |  |  | %MW979.X15 - %MW979.X8
980 | 40491 | %MX980.7 - %MX980.0 | %MB980 | %MW490 | %MD245 | %MW980.X07 - %MW980.X0 | %MW490 | %MD490
981 |  | %MX981.7 - %MX981.0 | %MB981 |  |  | %MW981.X15 - %MW981.X8
982 | 40492 | %MX982.7 - %MX982.0 | %MB982 | %MW491 |  | %MW982.X07 - %MW982.X0 | %MW491
983 |  | %MX983.7 - %MX983.0 | %MB983 |  |  | %MW983.X15 - %MW983.X8
984 | 40493 | %MX984.7 - %MX984.0 | %MB984 | %MW492 | %MD246 | %MW984.X07 - %MW984.X0 | %MW492 | %MD492
985 |  | %MX985.7 - %MX985.0 | %MB985 |  |  | %MW985.X15 - %MW985.X8
986 | 40494 | %MX986.7 - %MX986.0 | %MB986 | %MW493 |  | %MW986.X07 - %MW986.X0 | %MW493
987 |  | %MX987.7 - %MX987.0 | %MB987 |  |  | %MW987.X15 - %MW987.X8
988 | 40495 | %MX988.7 - %MX988.0 | %MB988 | %MW494 | %MD247 | %MW988.X07 - %MW988.X0 | %MW494 | %MD494
989 |  | %MX989.7 - %MX989.0 | %MB989 |  |  | %MW989.X15 - %MW989.X8
990 | 40496 | %MX990.7 - %MX990.0 | %MB990 | %MW495 |  | %MW990.X07 - %MW990.X0 | %MW495
991 |  | %MX991.7 - %MX991.0 | %MB991 |  |  | %MW991.X15 - %MW991.X8
992 | 40497 | %MX992.7 - %MX992.0 | %MB992 | %MW496 | %MD248 | %MW992.X07 - %MW992.X0 | %MW496 | %MD496
993 |  | %MX993.7 - %MX993.0 | %MB993 |  |  | %MW993.X15 - %MW993.X8
994 | 40498 | %MX994.7 - %MX994.0 | %MB994 | %MW497 |  | %MW994.X07 - %MW994.X0 | %MW497
995 |  | %MX995.7 - %MX995.0 | %MB995 |  |  | %MW995.X15 - %MW995.X8
996 | 40499 | %MX996.7 - %MX996.0 | %MB996 | %MW498 | %MD249 | %MW996.X07 - %MW996.X0 | %MW498 | %MD498
997 |  | %MX997.7 - %MX997.0 | %MB997 |  |  | %MW997.X15 - %MW997.X8
998 | 40500 | %MX998.7 - %MX998.0 | %MB998 | %MW499 |  | %MW998.X07 - %MW998.X0 | %MW499
999 |  | %MX999.7 - %MX999.0 | %MB999 |  |  | %MW999.X15 - %MW999.X8
myBool AT %MX0.0 : BOOL; //Boolean Type myInput AT %IX0.0 : BOOL; myOut AT %QX0.0 : BOOL; myByte AT %MB0 : BYTE; //Byte Type mySINT AT %MB0 : SINT; myUSINT AT %MB0 : USINT; myByteArary AT %MB0 : ARRAY[0..10] OF BYTE; myWORD AT %MW0 : WORD; //16 bit types myINT AT %MW0 : INT; myUINT AT %MW0 : UINT; myWordArary AT %MW0 : ARRAY[0..10] OF WORD; myDWORD AT %MD0 : DWORD; //32bit Types myDINT AT %MD0 : DINT; myUDINT AT %MD0 : UDINT; myReal AT %MD0 : REAL; myDwordArray AT %MD0 : ARRAY[0..10] OF DWORD; mySTRING AT %MB0 : STRING; //STRING